## FDU-VFX2.1 English
CG Drives & Automation Box 222 25 SE-250 24 Helsingborg Sweden www.emotron.com / www.cgglobal.com
|  | = Only valid for Emotron FDU2.1 | [7 empty] | See Instruction Manual (Sections 8 and 9) for format description
= Only valid for Emotron VFX2.1
FDU-VFX2.1 V5.12 Parameters | [5 empty] | Modbus instance / DeviceNet nbr | Profibus slot / index | EtherCAT index (HEX) | Profinet index | Fieldbus format | Modbus format | Comments selection/unit NOTE: Not in print area
100 |  |  |  |  | StartWindow
| 110 |  |  |  | 1st Line | 43001 | 168/160 | 4BB9 | 19385 | UInt | UInt | 0=Process Val, 1=Speed, 2=Torque, 3=Process Ref, 4=Shaft Power, 5=El Power, 6=Current, 7=Output volt, 8=Frequency, 9=DC Voltage, 10=IGBT Temp, 11=Motor Temp, 12=VSD Status, 13=Run Time, 14=Energy, 15=Mains Time, 16=Enc Speed, 17=Unit Name, 18=Time, 19=Date
| 120 |  |  |  | 2nd Line | 43002 | 168/161 | 4BBA | 19386 | UInt | UInt | 0=Process Val, 1=Speed, 2=Torque, 3=Process Ref, 4=Shaft Power, 5=El Power, 6=Current, 7=Output volt, 8=Frequency, 9=DC Voltage, 10=IGBT Temp, 11=Motor Temp, 12=VSD Status, 13=Run Time, 14=Energy, 15=Mains Time, 16=Enc Speed, 17=Unit Name, 18=Time, 19=Date
| 130 |  |  |  | 3rd Line | 43003 | 168/162 | 4BBB | 19387 | UInt | UInt | 0=Process Val, 1=Speed, 2=Torque, 3=Process Ref, 4=Shaft Power, 5=El Power, 6=Current, 7=Output volt, 8=Frequency, 9=DC Voltage, 10=IGBT Temp, 11=Motor Temp, 12=VSD Status, 13=Run Time, 14=Energy, 15=Mains Time, 16=Enc Speed, 17=Unit Name, 18=Time, 19=Date
| 140 |  |  |  | 4th Line | 43004 | 168/163 | 4BBC | 19388 | UInt | UInt | 0=Process Val, 1=Speed, 2=Torque, 3=Process Ref, 4=Shaft Power, 5=El Power, 6=Current, 7=Output volt, 8=Frequency, 9=DC Voltage, 10=IGBT Temp, 11=Motor Temp, 12=VSD Status, 13=Run Time, 14=Energy, 15=Mains Time, 16=Enc Speed, 17=Unit Name, 18=Time, 19=Date
| 150 |  |  |  | 5th Line | 43005 | 168/164 | 4BBD | 19389 | UInt | UInt | 0=Process Val, 1=Speed, 2=Torque, 3=Process Ref, 4=Shaft Power, 5=El Power, 6=Current, 7=Output volt, 8=Frequency, 9=DC Voltage, 10=IGBT Temp, 11=Motor Temp, 12=VSD Status, 13=Run Time, 14=Energy, 15=Mains Time, 16=Enc Speed, 17=Unit Name, 18=Time, 19=Date
| 160 |  |  |  | 6th Line | 43006 | 168/165 | 4BBE | 19390 | UInt | UInt | 0=Process Val, 1=Speed, 2=Torque, 3=Process Ref, 4=Shaft Power, 5=El Power, 6=Current, 7=Output volt, 8=Frequency, 9=DC Voltage, 10=IGBT Temp, 11=Motor Temp, 12=VSD Status, 13=Run Time, 14=Energy, 15=Mains Time, 16=Enc Speed, 17=Unit Name, 18=Time, 19=Date
| 170 |  |  |  | View mode | 43007 | 168/166 | 4BBF | 19391 | UInt | UInt | 0=Normal 100, 1=Always 100+, 2=Normal 100wo
200 |  |  |  |  | Main Setup
| 210 |  |  |  | Operation
|  | 211 |  |  | Language | 43011 | 168/170 | 4BC3 | 19395 | UInt | UInt | 0=English, 1=Svenska, 2=Nederlands, 3=Deutsch, 4=Français, 5=Español, 6=Pyccкий, 7=Italiano, 8=Česky, 9=Turkish, 10=Português, 11=Polski
|  | 212 |  |  | Select Motor | 43012 | 168/171 | 4BC4 | 19396 | UInt | UInt | 0=M1, 1=M2, 2=M3, 3=M4
|  | 213 |  |  | Drive Mode | 43013 | 168/172 | 4BC5 | 19397 | UInt | UInt | 0=Speed, 1=Torque, 2=V/Hz, 3=Spare, 4=Speed (PWM), 5=Torque (PWM), 6=V/Hz (VFX)
|  | 214 |  |  | Ref Control | 43014 | 168/173 | 4BC6 | 19398 | UInt | UInt | 0=Remote, 1=Keyboard, 2=Com, 3=Option
|  | 215 |  |  | Run/Stp Ctrl | 43015 | 168/174 | 4BC7 | 19399 | UInt | UInt | 0=Remote, 1=Keyboard, 2=Com, 3=Option
|  | 216 |  |  | Reset Ctrl | 43016 | 168/175 | 4BC8 | 19400 | UInt | UInt | 0=Remote, 1=Keyboard, 2=Com, 3=Remote+Keyb, 4=Com+Keyb, 5=Rem+Keyb+Com, 6=Option
|  | 217 |  |  | Local/Rem
|  |  | 2171 |  | LocRefCtrl | 43009 | 168/168 | 4BC1 | 19393 | UInt | UInt | 0=Standard, 1=Remote, 2=Keyboard, 3=Com, 4=Option
|  |  | 2172 |  | LocRunCtrl | 43010 | 168/169 | 4BC2 | 19394 | UInt | UInt | 0=Standard, 1=Remote, 2=Keyboard, 3=Com, 4=Option
|  | 218 |  |  | Lock Code? | 43018 | 168/177 | 4BCA | 19402 | UInt, 1=1 | UInt | 1
|  | 219 |  |  | Rotation | 43019 | 168/178 | 4BCB | 19403 | UInt | UInt | 0=-, 1=R, 2=L, 3=R+L
|  | 21A |  |  | Level/Edge | 43020 | 168/179 | 4BCC | 19404 | UInt | UInt | 0=Level, 1=Edge
|  | 21B |  |  | Supply Volts | 43381 | 170/30 | 4D35 | 19765 | UInt | UInt | 0=Standard, 1=220-240VAC, 2=Not Valid, 3=380-415VAC, 4=440-480VAC, 5=500-525VAC, 6=550-600VAC, 7=660-690VAC
|  | 21C |  |  | Supply Type | 43382 | 170/31 | 4D36 | 19766 | UInt | UInt | 0=AC Supply, 1=AFE Supply, 2=DC Supply, 3=AC/DC Suppl
|  | 21D |  |  | Fire Mode | 49333 | 193/117 | 6475 | 25717 | UInt | UInt | 0=Off, 1=On, 2=DigIn
|  | 21E |  |  | CP Units
|  |  | 21E1 |  | CP Unit Torq | 43383 | 170/32 | 4D37 | 19767 | UInt | UInt | 0=Nm, 1=LbFt
|  |  | 21E2 |  | CP Unit Pow | 43384 | 170/33 | 4D38 | 19768 | UInt | UInt | 0=W, 1=hp
|  |  | 21E3 |  | CP Unit Temp | 43385 | 170/34 | 4D39 | 19769 | UInt | UInt | 0=°C, 1=°F
| 220 |  |  |  | Motor Data
|  | 221 |  |  | Motor Volts | 43041 | 168/200 | 4BE1 | 19425 | Long, 1=0.1V | EInt | 0.1V
|  | 222 |  |  | Motor Freq | 43060 | 168/219 | 4BF4 | 19444 | Long, 1=0.1Hz | EInt | 0.1Hz
|  | 223 |  |  | Motor Power | 43043 | 168/202 | 4BE3 | 19427 | Long, 1=1W | EInt | 1W
|  | 224 |  |  | Motor Curr | 43044 | 168/203 | 4BE4 | 19428 | Long, 1=0.1A | EInt | 0.1A
|  | 225 |  |  | Motor Speed | 43045 | 168/204 | 4BE5 | 19429 | UInt, 1=1rpm | UInt | 1rpm
|  | 226 |  |  | Motor Poles | 43046 | 168/205 | 4BE6 | 19430 | Long, 1=1 | EInt | 1
|  | 227 |  |  | Motor Cosφ | 43047 | 168/206 | 4BE7 | 19431 | Long, 1=0.01 | EInt | 0.01
|  | 228 |  |  | Motor Vent | 43048 | 168/207 | 4BE8 | 19432 | UInt | UInt | 0=None, 1=Self, 2=Forced
|  | 229 |  |  | Motor ID-Run | 43049 | 168/208 | 4BE9 | 19433 | UInt | UInt | 0=Off, 1=Short, 2=Extended
|  | 22A |  |  | Motor Sound | 43050 | 168/209 | 4BEA | 19434 | UInt | UInt | 0=E, 1=F, 2=G, 3=H, 4=Advanced
|  | 22B |  |  | Encoder | 43051 | 168/210 | 4BEB | 19435 | UInt | UInt | 0=Off, 1=On, 2=Off Inverted, 3=On Inverted
|  | 22C |  |  | Enc Pulses | 43052 | 168/211 | 4BEC | 19436 | Long, 1=1 | EInt | 1
|  | 22D |  |  | Enc Speed | 42911 | 168/70 | 4B5F | 19295 | Int, 1=1rpm | Int | 1rpm
|  | 22E |  |  | Motor PWM
|  |  | 22E1 |  | PWM Fswitch | 43053 | 168/212 | 4BED | 19437 | UInt, 1=1Hz | UInt | 1Hz
|  |  | 22E2 |  | PWM Mode | 43054 | 168/213 | 4BEE | 19438 | UInt | UInt | 0=Standard, 1=Sine Filt
|  |  | 22E3 |  | PWM Random | 43055 | 168/214 | 4BEF | 19439 | UInt | UInt | 0=Off, 1=On
|  |  | 22E4 |  | Udc filter | 43040 | 168/199 | 4BE0 | 19424 | UInt | UInt | 0=Off, 1=On
|  | 22F |  |  | Enc Puls Ctr | 42912 | 168/71 | 4B60 | 19296 | Long, 1=1 | Int | 1
|  | 22G |  |  | Enc Fault
|  |  | 22G1 |  | Enc F Delay | 43056 | 168/215 | 4BF0 | 19440 | Long, 1=0.01s | EInt | 0.01s
|  |  | 22G2 |  | Enc F Band | 43057 | 168/216 | 4BF1 | 19441 | Long, 1=1% | EInt | 1%
|  |  | 22G3 |  | Max EncFCtr | 42913 | 168/72 | 4B61 | 19297 | Long, 1=0.001s | EInt | 0.001s
|  |  | 22G4 |  | EncOverrule | 43068 | 168/227 | 4BFC | 19452 | UInt | UInt | 0=Off, 1=On
|  | 22H |  |  | Phase Order | 43058 | 168/217 | 4BF2 | 19442 | UInt | UInt | 0=Normal, 1=Reverse
|  | 22I |  |  | Motor Type | 43059 | 168/218 | 4BF3 | 19443 | UInt | UInt | 0=Async, 1=PMSM, 2=Sync Rel
|  | 22J |  |  | Extend Data
|  |  | 22J1 |  | BEMF | 43391 | 170/40 | 4D3F | 19775 | Long, 1=0.1V | EInt | 0.1V
|  |  | 22J2 |  | Rs (mΩ/ph) | 43392 | 170/41 | 4D40 | 19776 | Long, 1=0.001 | EInt | 0.001
|  |  | 22J3 |  | Lsd (mH/ph) | 43393 | 170/42 | 4D41 | 19777 | Long, 1=0.001 | EInt | 0.001
|  |  | 22J4 |  | Lsq (mH/ph) | 43394 | 170/43 | 4D42 | 19778 | Long, 1=0.001 | EInt | 0.001
| 230 |  |  |  | Mot Protect
|  | 231 |  |  | Mot I²t Type | 43061 | 168/220 | 4BF5 | 19445 | UInt | UInt | 0=Off, 1=Trip, 2=Limit T, 3=Limit Spd
|  | 232 |  |  | Mot I²t Curr | 43062 | 168/221 | 4BF6 | 19446 | Long, 1=1% | EInt | 1%
|  | 233 |  |  | Mot I²t Time | 43063 | 168/222 | 4BF7 | 19447 | Long, 1=1s | EInt | 1s
|  | 234 |  |  | Thermal Prot | 43064 | 168/223 | 4BF8 | 19448 | UInt | UInt | 0=Off, 1=1xPTC, 2=PT100, 3=1xPTC+PT100, 4=2xPTC, 5=2xPTC+PT100
|  | 235 |  |  | Motor Class | 43065 | 168/224 | 4BF9 | 19449 | UInt | UInt | 0=A 100°C, 1=E 115°C, 2=B 120°C, 3=F 140°C, 4=F Nema 145°C, 5=H 165°C
|  | 236 |  |  | PT100 Inputs | 43066 | 168/225 | 4BFA | 19450 | UInt | UInt | 0=-, 1=PT100 1, 2=PT100 2, 3=PT100 1+2, 4=PT100 3, 5=PT100 1+3, 6=PT100 2+3, 7=PT100 1+2+3, 8=PT100 1-4, 9=PT100 1-5, 10=PT100 1-6
|  | 237 |  |  | Motor PTC | 43067 | 168/226 | 4BFB | 19451 | UInt | UInt | 0=Off, 1=On
|  | 238 |  |  | I²t Min Spd | 43386 | 170/35 | 4D3A | 19770 | UInt, 1=1rpm | UInt | 1rpm
| 240 |  |  |  | Set Handling
|  | 241 |  |  | Select Set | 43022 | 168/181 | 4BCE | 19406 | UInt | UInt | 0=A, 1=B, 2=C, 3=D, 4=DigIn, 5=Com, 6=Option
|  | 242 |  |  | Copy Set | 43021 | 168/180 | 4BCD | 19405 | UInt | UInt | 0=A>B, 1=A>C, 2=A>D, 3=B>A, 4=B>C, 5=B>D, 6=C>A, 7=C>B, 8=C>D, 9=D>A, 10=D>B, 11=D>C
|  | 243 |  |  | Default>Set | 43023 | 168/182 | 4BCF | 19407 | UInt | UInt | 0=A, 1=B, 2=C, 3=D, 4=ABCD, 5=Factory, 6=M1, 7=M2, 8=M3, 9=M4, 10=M1M2M3M4
|  | 244 |  |  | Copy to CP | 43024 | 168/183 | 4BD0 | 19408 | UInt | UInt | 0=No Copy, 1=Copy
|  | 245 |  |  | Load from CP | 43025 | 168/184 | 4BD1 | 19409 | UInt | UInt | 0=No Copy, 1=A, 2=B, 3=C, 4=D, 5=ABCD, 6=A+Mot, 7=B+Mot, 8=C+Mot, 9=D+Mot, 10=ABCD+Mot, 11=M1, 12=M2, 13=M3, 14=M4, 15=M1M2M3M4, 16=All
|  | 246 |  |  | ComFlt Set | 42653 | 167/67 | 4A5D | 19037 | UInt | UInt | 0=A, 1=B, 2=C, 3=D, 4=DigIn, 5=Keep Last
|  | 247 |  |  | AnInFlt Set | 42654 | 167/68 | 4A5E | 19038 | UInt | UInt | 0=A, 1=B, 2=C, 3=D, 4=DigIn, 5=Keep Last
| 250 |  |  |  | Autoreset
|  | 251 |  |  | Autores Ctrl
|  |  | 2511 |  | No of Trips | 43071 | 168/230 | 4BFF | 19455 | UInt, 1=1 | UInt | 1
|  |  | 2512 |  | Autores Enb | 43069 | 168/228 | 4BFD | 19453 | UInt | UInt | 0=DigIn, 1=On
|  | 252 |  |  | DriveProtect
|  |  | 2521 |  | Over temp | 43072 | 168/231 | 4C00 | 19456 | Long, 1=1s | EInt | 1s
|  |  | 2522 |  | Over volt D | 43075 | 168/234 | 4C03 | 19459 | Long, 1=1s | EInt | 1s
|  |  | 2523 |  | Over volt G | 43076 | 168/235 | 4C04 | 19460 | Long, 1=1s | EInt | 1s
|  |  | 2524 |  | Over volt | 43077 | 168/236 | 4C05 | 19461 | Long, 1=1s | EInt | 1s
|  |  | 2525 |  | Undervoltage | 43088 | 168/247 | 4C10 | 19472 | Long, 1=1s | EInt | 1s
|  |  | 2526 |  | Over curr F | 43082 | 168/241 | 4C0A | 19466 | Long, 1=1s | EInt | 1s
|  |  | 2527 |  | Power fault | 43087 | 168/246 | 4C0F | 19471 | Long, 1=1s | EInt | 1s
|  |  | 2528 |  | LC Level | 43099 | 169/3 | 4C1B | 19483 | Long, 1=1s | EInt | 1s
|  |  | 2529 |  | LC Level TT | 43100 | 169/4 | 4C1C | 19484 | UInt | UInt | 0=Trip, 1=Deceleration
|  | 253 |  |  | MotorProtect
|  |  | 2531 |  | Motor Lost | 43083 | 168/242 | 4C0B | 19467 | Long, 1=1s | EInt | 1s
|  |  | 2532 |  | Locked Rotor | 43086 | 168/245 | 4C0E | 19470 | Long, 1=1s | EInt | 1s
|  |  | 2533 |  | Motor I²t | 43073 | 168/232 | 4C01 | 19457 | Long, 1=1s | EInt | 1s
|  |  | 2534 |  | Motor I²t TT | 43074 | 168/233 | 4C02 | 19458 | UInt | UInt | 0=Trip, 1=Deceleration
|  |  | 2535 |  | PT100 | 43078 | 168/237 | 4C06 | 19462 | Long, 1=1s | EInt | 1s
|  |  | 2536 |  | PT100 TT | 43079 | 168/238 | 4C07 | 19463 | UInt | UInt | 0=Trip, 1=Deceleration
|  |  | 2537 |  | PTC | 43084 | 168/243 | 4C0C | 19468 | Long, 1=1s | EInt | 1s
|  |  | 2538 |  | PTC TT | 43085 | 168/244 | 4C0D | 19469 | UInt | UInt | 0=Trip, 1=Deceleration
|  |  | 2539 |  | Over speed | 43096 | 169/0 | 4C18 | 19480 | Long, 1=1s | EInt | 1s
|  |  | 253A |  | Ext Mot Temp | 43097 | 169/1 | 4C19 | 19481 | Long, 1=1s | EInt | 1s
|  |  | 253B |  | Ext Mot TT | 43098 | 169/2 | 4C1A | 19482 | UInt | UInt | 0=Trip, 1=Deceleration
|  |  | 253C |  | Brk Fault | 43070 | 168/229 | 4BFE | 19454 | Long, 1=1s | EInt | 1s
|  |  | 253D |  | Encoder | 43561 | 170/210 | 4DE9 | 19945 | Long, 1=1s | EInt | 1s
|  | 254 |  |  | Comm & I/O
|  |  | 2541 |  | Com Error | 43089 | 168/248 | 4C11 | 19473 | Long, 1=1s | EInt | 1s
|  |  | 2542 |  | Com Error TT | 43090 | 168/249 | 4C12 | 19474 | UInt | UInt | 0=Trip, 1=Deceleration
|  |  | 2543 |  | AnIn<Offset | 43566 | 170/215 | 4DEE | 19950 | Long, 1=1s | EInt | 1s
|  |  | 2544 |  | AnIn TT | 43567 | 170/216 | 4DEF | 19951 | UInt | UInt | 0=Trip, 1=Deceleration
|  | 255 |  |  | Load monitor
|  |  | 2551 |  | Min Alarm | 43091 | 168/250 | 4C13 | 19475 | Long, 1=1s | EInt | 1s
|  |  | 2552 |  | Min Alarm TT | 43092 | 168/251 | 4C14 | 19476 | UInt | UInt | 0=Trip, 1=Deceleration
|  |  | 2553 |  | Max Alarm | 43093 | 168/252 | 4C15 | 19477 | Long, 1=1s | EInt | 1s
|  |  | 2554 |  | Max Alarm TT | 43094 | 168/253 | 4C16 | 19478 | UInt | UInt | 0=Trip, 1=Deceleration
|  | 256 |  |  | Pump
|  |  | 2561 |  | Pump | 43095 | 168/254 | 4C17 | 19479 | Long, 1=1s | EInt | 1s
|  | 257 |  |  | Crane
|  |  | 2571 |  | Crane Deviat | 43562 | 170/211 | 4DEA | 19946 | Long, 1=1s | EInt | 1s
|  |  | 2572 |  | Crane Comm | 43563 | 170/212 | 4DEB | 19947 | Long, 1=1s | EInt | 1s
|  | 258 |  |  | External
|  |  | 2581 |  | Ext Trip 1 | 43080 | 168/239 | 4C08 | 19464 | Long, 1=1s | EInt | 1s
|  |  | 2582 |  | ExtTrip1 TT | 43081 | 168/240 | 4C09 | 19465 | UInt | UInt | 0=Trip, 1=Deceleration
|  |  | 2583 |  | Ext Trip 2 | 43564 | 170/213 | 4DEC | 19948 | Long, 1=1s | EInt | 1s
|  |  | 2584 |  | ExtTrip2 TT | 43565 | 170/214 | 4DED | 19949 | UInt | UInt | 0=Trip, 1=Deceleration
|  |  | 2585 |  | Ext Trip 3 | 43568 | 170/217 | 4DF0 | 19952 | Long, 1=1s | EInt | 1s
|  |  | 2586 |  | ExtTrip3 TT | 43569 | 170/218 | 4DF1 | 19953 | UInt | UInt | 0=Trip, 1=Deceleration
|  |  | 2587 |  | Ext Trip 4 | 43570 | 170/219 | 4DF2 | 19954 | Long, 1=1s | EInt | 1s
|  |  | 2588 |  | ExtTrip4 TT | 43571 | 170/220 | 4DF3 | 19955 | UInt | UInt | 0=Trip, 1=Deceleration
| 260 |  |  |  | Serial Com
|  | 261 |  |  | Com Type | 43031 | 168/190 | 4BD7 | 19415 | UInt | UInt | 0=RS232/485, 1=Fieldbus
|  | 262 |  |  | RS232/485
|  |  | 2621 |  | Baudrate | 43032 | 168/191 | 4BD8 | 19416 | UInt | UInt | 0=2400, 1=4800, 2=9600, 3=19200, 4=38400, 5=57600, 6=115200
|  |  | 2622 |  | Address | 43033 | 168/192 | 4BD9 | 19417 | UInt, 1=1 | UInt | 1
|  | 263 |  |  | Fieldbus
|  |  | 2631 |  | Address | 43034 | 168/193 | 4BDA | 19418 | UInt, 1=1 | UInt | 1
|  |  | 2632 |  | PrData Mode | 43035 | 168/194 | 4BDB | 19419 | UInt | UInt | 0=None, 1=None, 2=None, 3=None, 4=Basic, 5=Basic, 6=Basic, 7=Basic, 8=Extended
|  |  | 2633 |  | Read/Write | 43036 | 168/195 | 4BDC | 19420 | UInt | UInt | 0=RW, 1=Read
|  |  | 2634 |  | AddPrValues | 43039 | 168/198 | 4BDF | 19423 | UInt, 1=1 | UInt | 1
|  |  | 2635 |  | CANBaudrate | 43030 | 168/189 | 4BD6 | 19414 | UInt, 1=1 | UInt | 1
|  | 264 |  |  | Com Fault
|  |  | 2641 |  | ComFlt Mode | 43037 | 168/196 | 4BDD | 19421 | UInt | UInt | 0=Off, 1=Trip, 2=Warning, 3=Change PSet
|  |  | 2642 |  | ComFlt Time | 43038 | 168/197 | 4BDE | 19422 | Long, 1=0.1s | EInt | 0.1s
|  |  | 2643 |  | 485Flt Mode | 42979 | 168/138 | 4BA3 | 19363 | UInt | UInt | 0=Off, 1=Trip, 2=Warning, 3=Change PSet
|  |  | 2644 |  | 485Flt Time | 42980 | 168/139 | 4BA4 | 19364 | Long, 1=0.1s | EInt | 0.1s
|  |  | 2645 |  | KbdComFMode | 42981 | 168/140 | 4BA5 | 19365 | UInt | UInt | 0=Off, 1=Trip, 2=Warning
|  |  | 2646 |  | KbdComFTime | 42982 | 168/141 | 4BA6 | 19366 | UInt, 1=0.1s | UInt | 0.1s
|  |  | 2647 |  | CPportFMode | 42983 | 168/142 | 4BA7 | 19367 | UInt | UInt | 0=Off, 1=Trip, 2=Warning, 3=Change PSet
|  |  | 2648 |  | CPportFTime | 42984 | 168/143 | 4BA8 | 19368 | UInt, 1=0.1s | UInt | 0.1s
|  | 265 |  |  | Ethernet
|  |  | 2651 |  | IP Address | 42701 | 167/115 | 4A8D | 19085 | UInt, 1=1 | UInt | 1, MSB
[6 empty] | 42702 | 167/116 | 4A8E | 19086 | UInt, 1=1 | UInt | 1
[6 empty] | 42703 | 167/117 | 4A8F | 19087 | UInt, 1=1 | UInt | 1
[6 empty] | 42704 | 167/118 | 4A90 | 19088 | UInt, 1=1 | UInt | 1, LSB
|  |  | 2652 |  | MAC Address | 42705 | 167/119 | 4A91 | 19089 | UInt, 1=1 | UInt | 1, MSB
[6 empty] | 42706 | 167/120 | 4A92 | 19090 | UInt, 1=1 | UInt | 1
[6 empty] | 42707 | 167/121 | 4A93 | 19091 | UInt, 1=1 | UInt | 1
[6 empty] | 42708 | 167/122 | 4A94 | 19092 | UInt, 1=1 | UInt | 1
[6 empty] | 42709 | 167/123 | 4A95 | 19093 | UInt, 1=1 | UInt | 1
[6 empty] | 42710 | 167/124 | 4A96 | 19094 | UInt, 1=1 | UInt | 1, LSB
|  |  | 2653 |  | Subnet Mask | 42711 | 167/125 | 4A97 | 19095 | UInt, 1=1 | UInt | 1, MSB
[6 empty] | 42712 | 167/126 | 4A98 | 19096 | UInt, 1=1 | UInt | 1
[6 empty] | 42713 | 167/127 | 4A99 | 19097 | UInt, 1=1 | UInt | 1
[6 empty] | 42714 | 167/128 | 4A9A | 19098 | UInt, 1=1 | UInt | 1, LSB
|  |  | 2654 |  | Gateway | 42715 | 167/129 | 4A9B | 19099 | UInt, 1=1 | UInt | 1, MSB
[6 empty] | 42716 | 167/130 | 4A9C | 19100 | UInt, 1=1 | UInt | 1
[6 empty] | 42717 | 167/131 | 4A9D | 19101 | UInt, 1=1 | UInt | 1
[6 empty] | 42718 | 167/132 | 4A9E | 19102 | UInt, 1=1 | UInt | 1, LSB
|  |  | 2655 |  | DHCP | 42719 | 167/133 | 4A9F | 19103 | UInt | UInt | 0=Off, 1=On
|  |  | 2656 |  | FTP Server | 42720 | 167/134 | 4AA0 | 19104 | UInt | UInt | 0=Off, 1=On
|  |  | 2657 |  | WEB Server | 42721 | 167/135 | 4AA1 | 19105 | UInt | UInt | 0=Off, 1=On
|  | 266 |  |  | FB Signal
|  |  | 2661 |  | FB S1/Wr1 | 42801 | 167/215 | 4AF1 | 19185 | UInt, 1=1 | UInt | 1
|  |  | 2662 |  | FB S2/Wr2 | 42802 | 167/216 | 4AF2 | 19186 | UInt, 1=1 | UInt | 1
|  |  | 2663 |  | FB S3/Wr3 | 42803 | 167/217 | 4AF3 | 19187 | UInt, 1=1 | UInt | 1
|  |  | 2664 |  | FB S4/Wr4 | 42804 | 167/218 | 4AF4 | 19188 | UInt, 1=1 | UInt | 1
|  |  | 2665 |  | FB S5/Wr5 | 42805 | 167/219 | 4AF5 | 19189 | UInt, 1=1 | UInt | 1
|  |  | 2666 |  | FB S6/Wr6 | 42806 | 167/220 | 4AF6 | 19190 | UInt, 1=1 | UInt | 1
|  |  | 2667 |  | FB S7/Wr7 | 42807 | 167/221 | 4AF7 | 19191 | UInt, 1=1 | UInt | 1
|  |  | 2668 |  | FB S8/Wr8 | 42808 | 167/222 | 4AF8 | 19192 | UInt, 1=1 | UInt | 1
|  |  | 2669 |  | FB S9/Rd1 | 42809 | 167/223 | 4AF9 | 19193 | UInt, 1=1 | UInt | 1
|  |  | 266A |  | FB S10/Rd2 | 42810 | 167/224 | 4AFA | 19194 | UInt, 1=1 | UInt | 1
|  |  | 266B |  | FB S11/Rd3 | 42811 | 167/225 | 4AFB | 19195 | UInt, 1=1 | UInt | 1
|  |  | 266C |  | FB S12/Rd4 | 42812 | 167/226 | 4AFC | 19196 | UInt, 1=1 | UInt | 1
|  |  | 266D |  | FB S13/Rd5 | 42813 | 167/227 | 4AFD | 19197 | UInt, 1=1 | UInt | 1
|  |  | 266E |  | FB S14/Rd6 | 42814 | 167/228 | 4AFE | 19198 | UInt, 1=1 | UInt | 1
|  |  | 266F |  | FB S15/Rd7 | 42815 | 167/229 | 4AFF | 19199 | UInt, 1=1 | UInt | 1
|  |  | 266G |  | FB S16/Rd8 | 42816 | 167/230 | 4B00 | 19200 | UInt, 1=1 | UInt | 1
|  | 269 |  |  | FB Status
|  |  | 2691 |  | Board Type | 31081 | 121/225 | 2439 | 1081 | UInt, 1=1 | UInt | 1
|  |  | 2692 |  | SUP-bit | 31082 | 121/226 | 243A | 1082 | UInt, 1=1 | UInt | 1
|  |  | 2693 |  | State FB | 31083 | 121/227 | 243B | 1083 | UInt, 1=1 | UInt | 1
|  |  | 2694 |  | Serial Nbr | 31079 | 121/223 | 2437 | 1079 | UInt, 1=1 | UInt | 1
|  |  | 2694 |  | Serial Nbr | 31080 | 121/224 | 2438 | 1080 | UInt, 1=1 | UInt | 1
|  |  | 2695 |  | FirmwareVer | 31084 | 121/228 | 243C | 1084 | UInt, 1=1 | UInt | 1
|  |  | 2696 |  | CRC errors | 31086 | 121/230 | 243E | 1086 | UInt, 1=1 | UInt | 1
|  |  | 2697 |  | MSG errors | 31087 | 121/231 | 243F | 1087 | UInt, 1=1 | UInt | 1
|  |  | 2698 |  | TOUT ctr | 31088 | 121/232 | 2440 | 1088 | UInt, 1=1 | UInt | 1
|  |  | 2699 |  | FB Input | 31089 | 121/233 | 2441 | 1089 | UInt, 1=1 | UInt | 1
|  |  | 269A |  | FB Output | 31090 | 121/234 | 2442 | 1090 | UInt, 1=1 | UInt | 1
|  |  | 269B |  | Last instno | 31091 | 121/235 | 2443 | 1091 | UInt, 1=1 | UInt | 1
| 270 |  |  |  | Wireless
|  | 271 |  |  | WirelessMode | 40200 | 157/164 | 40C8 | 16584 | UInt | UInt | 0=Off, 1=WiFi, 2=BLE
|  | 272 |  |  | WiFi Options
|  |  | 2721 |  | WiFi Mode | 40201 | 157/165 | 40C9 | 16585 | UInt | UInt | 0=AccessPoint, 1=Station
|  |  | 2722 |  | Channel | 40202 | 157/166 | 40CA | 16586 | UInt, 1=1 | UInt | 1
|  |  | 2723 |  | Encryption | 40203 | 157/167 | 40CB | 16587 | UInt | UInt | 0=Open, 1=WEP, 2=WPA-2
|  |  | 2724 |  | DHCP | 40204 | 157/168 | 40CC | 16588 | UInt | UInt | 0=Static, 1=DHCP
|  |  | 2725 |  | SSID | 40215 | 157/179 | 40D7 | 16599 | UInt | UInt
|  |  | 2726 |  | Password | 40235 | 157/199 | 40EB | 16619 | UInt | UInt
|  |  | 2727 |  | IP Address | 40255 | 157/219 | 40FF | 16639 | UInt, 1=1 | UInt | 1, MSB
[6 empty] | 40256 | 157/220 | 4100 | 16640 | UInt, 1=1 | UInt | 1
[6 empty] | 40257 | 157/221 | 4101 | 16641 | UInt, 1=1 | UInt | 1
[6 empty] | 40258 | 157/222 | 4102 | 16642 | UInt, 1=1 | UInt | 1, LSB
|  |  | 2728 |  | Subnet Mask | 40259 | 157/223 | 4103 | 16643 | UInt, 1=1 | UInt | 1, MSB
[6 empty] | 40260 | 157/224 | 4104 | 16644 | UInt, 1=1 | UInt | 1
[6 empty] | 40261 | 157/225 | 4105 | 16645 | UInt, 1=1 | UInt | 1
[6 empty] | 40262 | 157/226 | 4106 | 16646 | UInt, 1=1 | UInt | 1, LSB
|  |  | 2729 |  | Gateway | 40263 | 157/227 | 4107 | 16647 | UInt, 1=1 | UInt | 1, MSB
[6 empty] | 40264 | 157/228 | 4108 | 16648 | UInt, 1=1 | UInt | 1
[6 empty] | 40265 | 157/229 | 4109 | 16649 | UInt, 1=1 | UInt | 1
[6 empty] | 40266 | 157/230 | 410A | 16650 | UInt, 1=1 | UInt | 1, LSB
|  |  | 272A |  | WiFi Status | 30054 | 117/218 | 2036 | 54 | UInt | UInt | 0=OK, 1=Mode error, 2=AP pwd err, 3=SSID error, 4=SecPar err, 5=Sta Disconn, 6=NetConf err, 7=Config OK
|  | 273 |  |  | BLE Options
|  |  | 2731 |  | BluetoothID | 42620 | 167/34 | 4A3C | 19004 | UInt, 1=1 | UInt | 1
|  |  | 2732 |  | Pairing Key | 40267 | 157/231 | 410B | 16651 | UInt, 1=1 | UInt | 1
|  | 274 |  |  | Security
|  |  | 2741 |  | Sec. Mode | 40273 | 157/237 | 4111 | 16657 | UInt | UInt | 0=Open, 1=Password
|  |  | 2742 |  | Password | 40274 | 157/238 | 4112 | 16658 | UInt | UInt
300 |  |  |  |  | Process
| 310 |  |  |  | Set/View ref | 42991 | 168/150 | 4BAF | 19375 | Long, 1=0.001 | EInt | 1rpm, 1%, 1°C, 0.001 in [322]
| 320 |  |  |  | Proc Setting
|  | 321 |  |  | Proc Source | 43302 | 169/206 | 4CE6 | 19686 | UInt | UInt | 0=F(AnIn), 1=Speed, 2=Torque, 3=PT100, 4=F(Speed), 5=F(Torque), 6=F(Bus), 7=Frequency, 8=Option
|  | 322 |  |  | Proc Unit | 43303 | 169/207 | 4CE7 | 19687 | UInt | UInt | 0=Off, 1=%, 2=°C, 3=°F, 4=bar, 5=Pa, 6=Nm, 7=Hz, 8=rpm, 9=m³/h, 10=gal/h, 11=ft³/h, 12=User Defined
|  | 323 |  |  | User Unit | 43304 | 169/208 | 4CE8 | 19688 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 43305 | 169/209 | 4CE9 | 19689 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 43306 | 169/210 | 4CEA | 19690 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 43307 | 169/211 | 4CEB | 19691 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 43308 | 169/212 | 4CEC | 19692 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 43309 | 169/213 | 4CED | 19693 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
|  | 324 |  |  | Process Min | 43310 | 169/214 | 4CEE | 19694 | Long, 1=0.001 | EInt | 1rpm, 1%, 1°C, 0.001 in [322]
|  | 325 |  |  | Process Max | 43311 | 169/215 | 4CEF | 19695 | Long, 1=0.001 | EInt | 1rpm, 1%, 1°C, 0.001 in [322]
|  | 326 |  |  | Ratio | 43312 | 169/216 | 4CF0 | 19696 | UInt | UInt | 0=Linear, 1=Quadratic
|  | 327 |  |  | F(Val) PrMin | 43313 | 169/217 | 4CF1 | 19697 | Long, 1=1 | EInt | 1rpm, 1%
|  | 328 |  |  | F(Val) PrMax | 43314 | 169/218 | 4CF2 | 19698 | Long, 1=1 | EInt | 1rpm, 1%
| 330 |  |  |  | Start/Stop
|  | 331 |  |  | Acc Time | 43101 | 169/5 | 4C1D | 19485 | Long, 1=0.01s | EInt | 0.01s
|  | 332 |  |  | Dec Time | 43102 | 169/6 | 4C1E | 19486 | Long, 1=0.01s | EInt | 0.01s
|  | 333 |  |  | Acc MotPot | 43103 | 169/7 | 4C1F | 19487 | Long, 1=0.01s | EInt | 0.01s
|  | 334 |  |  | Dec MotPot | 43104 | 169/8 | 4C20 | 19488 | Long, 1=0.01s | EInt | 0.01s
|  | 335 |  |  | Acc<Min Spd | 43105 | 169/9 | 4C21 | 19489 | Long, 1=0.01s | EInt | 0.01s
|  | 336 |  |  | Dec<Min Spd | 43106 | 169/10 | 4C22 | 19490 | Long, 1=0.01s | EInt | 0.01s
|  | 337 |  |  | Acc Ramp | 43107 | 169/11 | 4C23 | 19491 | UInt | UInt | 0=Linear, 1=S-Curve
|  | 338 |  |  | Dec Ramp | 43108 | 169/12 | 4C24 | 19492 | UInt | UInt | 0=Linear, 1=S-Curve
|  | 339 |  |  | Start Mode | 43109 | 169/13 | 4C25 | 19493 | UInt | UInt | 0=Fast, 1=Normal DC
|  | 33A |  |  | Spinstart | 43110 | 169/14 | 4C26 | 19494 | UInt | UInt | 0=Off, 1=On, 2=Encoder
|  | 33B |  |  | Stop Mode | 43111 | 169/15 | 4C27 | 19495 | UInt | UInt | 0=Decel, 1=Coast
|  | 33C |  |  | Brk Release | 43112 | 169/16 | 4C28 | 19496 | Long, 1=0.01s | EInt | 0.01s
|  | 33D |  |  | Release Spd | 43113 | 169/17 | 4C29 | 19497 | Int, 1=1rpm | Int | 1rpm
|  | 33E |  |  | Brk Engage | 43114 | 169/18 | 4C2A | 19498 | Long, 1=0.01s | EInt | 0.01s
|  | 33F |  |  | Brk Wait | 43115 | 169/19 | 4C2B | 19499 | Long, 1=0.01s | EInt | 0.01s
|  | 33G |  |  | Vector Brake | 43116 | 169/20 | 4C2C | 19500 | UInt | UInt | 0=Off, 1=On
|  | 33H |  |  | Brk Fault | 43117 | 169/21 | 4C2D | 19501 | Long, 1=0.01s | EInt | 0.01s
|  | 33I |  |  | Release Trq | 43118 | 169/22 | 4C2E | 19502 | Long, 1=1% | EInt | 1%
|  | 33J |  |  | DC Hold
|  |  | 33J1 |  | DC Hold | 43148 | 169/52 | 4C4C | 19532 | UInt | UInt | 0=Off, 1=On
|  |  | 33J2 |  | DC Hold Spd | 43149 | 169/53 | 4C4D | 19533 | UInt, 1=1rpm | UInt | 1rpm
|  |  | 33J3 |  | DC Hold Cur | 43150 | 169/54 | 4C4E | 19534 | UInt, 1=1% | UInt | 1%
|  | 33K |  |  | Start Vector | 43119 | 169/23 | 4C2F | 19503 | UInt | UInt | 0=Normal (U), 1=Sequence, 2=Encoder
| 340 |  |  |  | Speed
|  | 341 |  |  | Min Speed | 43121 | 169/25 | 4C31 | 19505 | UInt, 1=1rpm | UInt | 1rpm
|  | 342 |  |  | Stp<MinSpd | 43122 | 169/26 | 4C32 | 19506 | Long, 1=0.01s | EInt | 0.01s
|  | 343 |  |  | Max Speed | 43123 | 169/27 | 4C33 | 19507 | UInt, 1=1rpm | UInt | 1rpm
|  | 344 |  |  | SkipSpd 1 Lo | 43124 | 169/28 | 4C34 | 19508 | UInt, 1=1rpm | UInt | 1rpm
|  | 345 |  |  | SkipSpd 1 Hi | 43125 | 169/29 | 4C35 | 19509 | UInt, 1=1rpm | UInt | 1rpm
|  | 346 |  |  | SkipSpd 2 Lo | 43126 | 169/30 | 4C36 | 19510 | UInt, 1=1rpm | UInt | 1rpm
|  | 347 |  |  | SkipSpd 2 Hi | 43127 | 169/31 | 4C37 | 19511 | UInt, 1=1rpm | UInt | 1rpm
|  | 348 |  |  | Jog Speed | 43128 | 169/32 | 4C38 | 19512 | Int, 1=1rpm | Int | 1rpm
|  | 349 |  |  | Droop Speed | 43120 | 169/24 | 4C30 | 19504 | Long, 1=0.01% | EInt | 0.01%
|  | 34A |  |  | OverSpdTrip | 43129 | 169/33 | 4C39 | 19513 | UInt, 1=1% | UInt | 1%
| 350 |  |  |  | Torques
|  | 351 |  |  | Max Torque | 43141 | 169/45 | 4C45 | 19525 | Long, 1=1% | EInt | 1%
|  | 352 |  |  | IxR Comp | 43142 | 169/46 | 4C46 | 19526 | UInt | UInt | 0=Off, 1=Automatic, 2=User defined
|  | 353 |  |  | IxR CompUsr | 43143 | 169/47 | 4C47 | 19527 | Long, 1=0.1% | EInt | 0.1%
|  | 354 |  |  | Flux optim | 43144 | 169/48 | 4C48 | 19528 | UInt | UInt | 0=Off, 1=On (Imin), 2=On (n,T), 3=On (cosφ)
|  | 355 |  |  | Max Power | 43145 | 169/49 | 4C49 | 19529 | Long, 1=1% | EInt | 1%
|  | 356 |  |  | Torque Ramp | 43146 | 169/50 | 4C4A | 19530 | UInt, 1=0.01s | UInt | 0.01s
| 360 |  |  |  | Preset Ref
|  | 361 |  |  | Motor Pot | 43131 | 169/35 | 4C3B | 19515 | UInt | UInt | 0=Volatile, 1=Non volatile
|  | 362 |  |  | Preset Ref 1 | 43132 | 169/36 | 4C3C | 19516 | Long, 1=0.001 | EInt | 1rpm, 1%, 1°C, 0.001 in [322]
|  | 363 |  |  | Preset Ref 2 | 43133 | 169/37 | 4C3D | 19517 | Long, 1=0.001 | EInt | 1rpm, 1%, 1°C, 0.001 in [322]
|  | 364 |  |  | Preset Ref 3 | 43134 | 169/38 | 4C3E | 19518 | Long, 1=0.001 | EInt | 1rpm, 1%, 1°C, 0.001 in [322]
|  | 365 |  |  | Preset Ref 4 | 43135 | 169/39 | 4C3F | 19519 | Long, 1=0.001 | EInt | 1rpm, 1%, 1°C, 0.001 in [322]
|  | 366 |  |  | Preset Ref 5 | 43136 | 169/40 | 4C40 | 19520 | Long, 1=0.001 | EInt | 1rpm, 1%, 1°C, 0.001 in [322]
|  | 367 |  |  | Preset Ref 6 | 43137 | 169/41 | 4C41 | 19521 | Long, 1=0.001 | EInt | 1rpm, 1%, 1°C, 0.001 in [322]
|  | 368 |  |  | Preset Ref 7 | 43138 | 169/42 | 4C42 | 19522 | Long, 1=0.001 | EInt | 1rpm, 1%, 1°C, 0.001 in [322]
|  | 369 |  |  | Key Ref Mode | 43139 | 169/43 | 4C43 | 19523 | UInt | UInt | 0=Normal, 1=MotPot, 2=MotPot+
| 370 |  |  |  | Spd Ctrl PI
|  | 371 |  |  | Spd PI Auto | 43151 | 169/55 | 4C4F | 19535 | UInt | UInt | 0=Off, 1=On
|  | 372 |  |  | Spd P Gain | 43152 | 169/56 | 4C50 | 19536 | Long, 1=0.1 | EInt | 0.1
|  | 373 |  |  | Spd I Time | 43153 | 169/57 | 4C51 | 19537 | Long, 1=0.01s | EInt | 0.01s
| 380 |  |  |  | ProcCtrl PID
|  | 381 |  |  | PID Control | 43154 | 169/58 | 4C52 | 19538 | UInt | UInt | 0=Off, 1=On, 2=Invert
|  | 383 |  |  | PID P Gain | 43156 | 169/60 | 4C54 | 19540 | Long, 1=0.1 | EInt | 0.1
|  | 384 |  |  | PID I Time | 43157 | 169/61 | 4C55 | 19541 | Long, 1=0.01s | EInt | 0.01s
|  | 385 |  |  | PID D Time | 43158 | 169/62 | 4C56 | 19542 | Long, 1=0.01s | EInt | 0.01s
|  | 386 |  |  | PID<MinSpd | 43371 | 170/20 | 4D2B | 19755 | Long, 1=0.01s | EInt | 0.01s
|  | 387 |  |  | PID Act Marg | 43372 | 170/21 | 4D2C | 19756 | Long, 1=0.001 | EInt | 1rpm, 1%, 1°C, 0.001 in [322]
|  | 388 |  |  | PID Stdy Tst | 43373 | 170/22 | 4D2D | 19757 | Long, 1=0.01s | EInt | 0.01s
|  | 389 |  |  | PID Stdy Mar | 43374 | 170/23 | 4D2E | 19758 | Long, 1=0.001 | EInt | 1rpm, 1%, 1°C, 0.001 in [322]
| 390 |  |  |  | EmoDedicPump
|  | 391 |  |  | Pump/Fan Ctl
|  |  | 3911 |  | Pump enable | 43161 | 169/65 | 4C59 | 19545 | UInt | UInt | 0=Off, 1=On
|  |  | 3912 |  | No of Drives | 43162 | 169/66 | 4C5A | 19546 | UInt, 1=1 | UInt | 1
|  |  | 3913 |  | Select Drive | 43163 | 169/67 | 4C5B | 19547 | UInt | UInt | 0=Sequence, 1=Run Time, 2=All
|  |  | 3914 |  | Change Cond | 43164 | 169/68 | 4C5C | 19548 | UInt | UInt | 0=Stop, 1=Timer, 2=Both, 3=Sync
|  |  | 3915 |  | Change Timer | 43165 | 169/69 | 4C5D | 19549 | UInt, 1=1h | UInt | 1h
|  |  | 3916 |  | Drives on Ch | 43166 | 169/70 | 4C5E | 19550 | UInt, 1=1 | UInt | 1
|  |  | 3917 |  | Upper Band | 43167 | 169/71 | 4C5F | 19551 | Long, 1=1% | EInt | 1%
|  |  | 3918 |  | Lower Band | 43168 | 169/72 | 4C60 | 19552 | Long, 1=1% | EInt | 1%
|  |  | 3919 |  | Start Delay | 43169 | 169/73 | 4C61 | 19553 | Long, 1=1s | EInt | 1s
|  |  | 391A |  | Stop Delay | 43170 | 169/74 | 4C62 | 19554 | Long, 1=1s | EInt | 1s
|  |  | 391B |  | Upp Band Lim | 43171 | 169/75 | 4C63 | 19555 | Long, 1=1% | EInt | 1%
|  |  | 391C |  | Low Band Lim | 43172 | 169/76 | 4C64 | 19556 | Long, 1=1% | EInt | 1%
|  |  | 391D |  | Settle Start | 43173 | 169/77 | 4C65 | 19557 | Long, 1=1s | EInt | 1s
|  |  | 391E |  | TransS Start | 43174 | 169/78 | 4C66 | 19558 | Long, 1=1% | EInt | 1%
|  |  | 391F |  | Settle Stop | 43175 | 169/79 | 4C67 | 19559 | Long, 1=1s | EInt | 1s
|  |  | 391G |  | TransS Stop | 43176 | 169/80 | 4C68 | 19560 | Long, 1=1% | EInt | 1%
|  |  | 391H |  | Run Time 1 | 31051 | 121/195 | 241B | 1051 | Long, 1=1h | EInt | 1h
[6 empty] | 31052 | 121/196 | 241C | 1052 | Long, 1=1m | EInt | 1m
[6 empty] | 31053 | 121/197 | 241D | 1053 | Long, 1=1s | EInt | 1s
|  |  |  | 391H1 | Rst Run Tm1 | 38 | 0/37 | 2026 | 38 | UInt | UInt | 0=No, 1=Yes
|  |  | 391I |  | Run Time 2 | 31054 | 121/198 | 241E | 1054 | Long, 1=1h | EInt | 1h
[6 empty] | 31055 | 121/199 | 241F | 1055 | Long, 1=1m | EInt | 1m
[6 empty] | 31056 | 121/200 | 2420 | 1056 | Long, 1=1s | EInt | 1s
|  |  |  | 391I1 | Rst Run Tm2 | 39 | 0/38 | 2027 | 39 | UInt | UInt | 0=No, 1=Yes
|  |  | 391J |  | Run Time 3 | 31057 | 121/201 | 2421 | 1057 | Long, 1=1h | EInt | 1h
[6 empty] | 31058 | 121/202 | 2422 | 1058 | Long, 1=1m | EInt | 1m
[6 empty] | 31059 | 121/203 | 2423 | 1059 | Long, 1=1s | EInt | 1s
|  |  |  | 391J1 | Rst Run Tm3 | 40 | 0/39 | 2028 | 40 | UInt | UInt | 0=No, 1=Yes
|  |  | 391K |  | Run Time 4 | 31060 | 121/204 | 2424 | 1060 | Long, 1=1h | EInt | 1h
[6 empty] | 31061 | 121/205 | 2425 | 1061 | Long, 1=1m | EInt | 1m
[6 empty] | 31062 | 121/206 | 2426 | 1062 | Long, 1=1s | EInt | 1s
|  |  |  | 391K1 | Rst Run Tm4 | 41 | 0/40 | 2029 | 41 | UInt | UInt | 0=No, 1=Yes
|  |  | 391L |  | Run Time 5 | 31063 | 121/207 | 2427 | 1063 | Long, 1=1h | EInt | 1h
[6 empty] | 31064 | 121/208 | 2428 | 1064 | Long, 1=1m | EInt | 1m
[6 empty] | 31065 | 121/209 | 2429 | 1065 | Long, 1=1s | EInt | 1s
|  |  |  | 391L1 | Rst Run Tm5 | 42 | 0/41 | 202A | 42 | UInt | UInt | 0=No, 1=Yes
|  |  | 391M |  | Run Time 6 | 31066 | 121/210 | 242A | 1066 | Long, 1=1h | EInt | 1h
[6 empty] | 31067 | 121/211 | 242B | 1067 | Long, 1=1m | EInt | 1m
[6 empty] | 31068 | 121/212 | 242C | 1068 | Long, 1=1s | EInt | 1s
|  |  |  | 391M1 | Rst Run Tm6 | 43 | 0/42 | 202B | 43 | UInt | UInt | 0=No, 1=Yes
|  |  | 391N |  | Pump 123456 | 31069 | 121/213 | 242D | 1069 | UInt, 1=1 | UInt | 1
|  |  | 391P |  | No of Backup | 43177 | 169/81 | 4C69 | 19561 | UInt, 1=1 | UInt | 1
|  |  | 391Q |  | MastChNoRamp | 43178 | 169/82 | 4C6A | 19562 | UInt | UInt | 0=Off, 1=On
|  | 392 |  |  | PumpCleaning
|  |  | 3921 |  | PC Enable | 43701 | 171/95 | 4E75 | 20085 | UInt | UInt | 0=Off, 1=On - Warn, 2=On - Trip
|  |  | 3922 |  | PC Allow | 43702 | 171/96 | 4E76 | 20086 | UInt | UInt | 0=Off, 1=On, 2=Once
|  |  | 392A |  | PC Trigger
|  |  |  | 392A1 | Force | 42898 | 168/57 | 4B52 | 19282 | UInt | UInt | 0=Off, 1=On
|  |  |  | 392A2 | EachStart | 43703 | 171/97 | 4E77 | 20087 | UInt | UInt | 0=Off, 1=On
|  |  |  | 392A3 | LoadMonMarg | 43704 | 171/98 | 4E78 | 20088 | Long, 1=1% | EInt | 1%
|  |  |  | 392A4 | LMTrigDelay | 43705 | 171/99 | 4E79 | 20089 | Long, 1=0.1s | EInt | 0.1s
|  |  |  | 392A5 | RunTime | 43706 | 171/100 | 4E7A | 20090 | UInt, 1=1h | UInt | 1h
|  |  |  | 392A6 | Interval | 43707 | 171/101 | 4E7B | 20091 | UInt, 1=1weeks | UInt | 1weeks
|  |  |  | 392A7 | Weekday | 43708 | 171/102 | 4E7C | 20092 | Long, 1=1 | EInt | 1
|  |  |  | 392A8 | StartTime | 43709 | 171/103 | 4E7D | 20093 | Long, 1=1h | EInt | 1h
[6 empty] | 43710 | 171/104 | 4E7E | 20094 | Long, 1=1m | EInt | 1m
[6 empty] | 43711 | 171/105 | 4E7F | 20095 | Long, 1=1s | EInt | 1s
|  |  |  | 392A9 | StartDate | 43712 | 171/106 | 4E80 | 20096 | Long, 1=1y | EInt | 1y
[6 empty] | 43713 | 171/107 | 4E81 | 20097 | Long, 1=1m | EInt | 1m
[6 empty] | 43714 | 171/108 | 4E82 | 20098 | Long, 1=1d | EInt | 1d
|  |  | 392B |  | PC Phase 1
|  |  |  | 392B1 | Ph1 Time | 43715 | 171/109 | 4E83 | 20099 | UInt, 1=1s | UInt | 1s
|  |  |  | 392B2 | Ph1 RefSpd | 43716 | 171/110 | 4E84 | 20100 | Int, 1=1% | Int | 1%
|  |  |  | 392B3 | Ph1 AccTime | 43717 | 171/111 | 4E85 | 20101 | Long, 1=0.1s | EInt | 0.1s
|  |  |  | 392B4 | Ph1 DecTime | 43718 | 171/112 | 4E86 | 20102 | Long, 1=0.1s | EInt | 0.1s
|  |  | 392C |  | PC Phase 2
|  |  |  | 392C1 | Ph2 Time | 43719 | 171/113 | 4E87 | 20103 | UInt, 1=1s | UInt | 1s
|  |  |  | 392C2 | Ph2 RefSpd | 43720 | 171/114 | 4E88 | 20104 | Int, 1=1% | Int | 1%
|  |  |  | 392C3 | Ph2 AccTime | 43721 | 171/115 | 4E89 | 20105 | Long, 1=0.1s | EInt | 0.1s
|  |  |  | 392C4 | Ph2 DecTime | 43722 | 171/116 | 4E8A | 20106 | Long, 1=0.1s | EInt | 0.1s
|  |  | 392D |  | PC Phase 3
|  |  |  | 392D1 | Ph3 Time | 43723 | 171/117 | 4E8B | 20107 | UInt, 1=1s | UInt | 1s
|  |  |  | 392D2 | Ph3 RefSpd | 43724 | 171/118 | 4E8C | 20108 | Int, 1=1% | Int | 1%
|  |  |  | 392D3 | Ph3 AccTime | 43725 | 171/119 | 4E8D | 20109 | Long, 1=0.1s | EInt | 0.1s
|  |  |  | 392D4 | Ph3 DecTime | 43726 | 171/120 | 4E8E | 20110 | Long, 1=0.1s | EInt | 0.1s
|  |  | 392E |  | PC MaxAttmpt | 43727 | 171/121 | 4E8F | 20111 | UInt, 1=1 | UInt | 1
|  |  | 392F |  | PC Status
|  |  |  | 392F1 | State | 31075 | 121/219 | 2433 | 1075 | UInt | UInt | 0=Off, 1=Requested, 2=Active
|  |  |  | 392F2 | AttmptCnt | 31076 | 121/220 | 2434 | 1076 | UInt, 1=1 | UInt | 1
|  |  |  | 392F3 | ResetCnt | 12 | 0/11 | 200C | 12 | UInt | UInt | 0=No, 1=Yes
|  |  |  | 392F4 | TotCnt | 31077 | 121/221 | 2435 | 1077 | UInt, 1=1 | UInt | 1
|  |  |  | 392F5 | TotCntSince | 31078 | 121/222 | 2436 | 1078 | UInt, 1=1h | UInt | 1h
|  |  |  | 392F6 | TotCntReset | 13 | 0/12 | 200D | 13 | UInt | UInt | 0=No, 1=Yes
| 3A0 |  |  |  | Crane Option
|  | 3A1 |  |  | Crane enable | 43181 | 169/85 | 4C6D | 19565 | UInt | UInt | 0=Off, 1=On
|  | 3A2 |  |  | Control | 43182 | 169/86 | 4C6E | 19566 | UInt | UInt | 0=4-speeds, 1=3-pos, 2=Analogue
|  | 3A3 |  |  | Crane Relay1 | 43183 | 169/87 | 4C6F | 19567 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  | 3A4 |  |  | Crane Relay2 | 43184 | 169/88 | 4C70 | 19568 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  | 3A5 |  |  | PreLimSwSpd | 43185 | 169/89 | 4C71 | 19569 | Int, 1=1rpm | Int | 1rpm
|  | 3A6 |  |  | CrawlSpd H/R | 43189 | 169/93 | 4C75 | 19573 | Int, 1=1rpm | Int | 1rpm
|  | 3A7 |  |  | CrawlSpd L/L | 43190 | 169/94 | 4C76 | 19574 | Int, 1=1rpm | Int | 1rpm
|  | 3A8 |  |  | Speed 2 | 43186 | 169/90 | 4C72 | 19570 | Int, 1=1rpm | Int | 1rpm
|  | 3A9 |  |  | Speed 3 | 43187 | 169/91 | 4C73 | 19571 | Int, 1=1rpm | Int | 1rpm
|  | 3AA |  |  | Speed 4 | 43188 | 169/92 | 4C74 | 19572 | Int, 1=1rpm | Int | 1rpm
|  | 3AB |  |  | Dev Bandwidt | 43191 | 169/95 | 4C77 | 19575 | Int, 1=1rpm | Int | 1rpm
|  | 3AC |  |  | Dev Time | 43192 | 169/96 | 4C78 | 19576 | Long, 1=0.001s | EInt | 0.001s
|  | 3AD |  |  | LAFS Load | 43193 | 169/97 | 4C79 | 19577 | Long, 1=1% | EInt | 1%
|  | 3AE |  |  | Crane Inputs | 39811 | 156/30 | 4653 | 9811 | UInt, 1=1 | UInt | 1
|  | 3AF |  |  | CraneOutputs | 39812 | 156/31 | 4654 | 9812 | UInt, 1=1 | UInt | 1
|  | 3AG |  |  | Crane N Func | 43194 | 169/98 | 4C7A | 19578 | UInt | UInt | 0=Off, 1=Zero pos, 2=Brk Ackn
400 |  |  |  |  | Monitor/Prot
| 410 |  |  |  | Load Monitor
|  | 411 |  |  | Alarm Select | 43321 | 169/225 | 4CF9 | 19705 | UInt | UInt | 0=Off, 1=Min, 2=Max, 3=Min+Max
|  | 412 |  |  | Alarm Trip | 43322 | 169/226 | 4CFA | 19706 | UInt | UInt | 0=Off, 1=Min, 2=Max, 3=Min+Max
|  | 413 |  |  | Ramp Alarm | 43323 | 169/227 | 4CFB | 19707 | UInt | UInt | 0=Off, 1=On
|  | 414 |  |  | Start Delay | 43324 | 169/228 | 4CFC | 19708 | Long, 1=1s | EInt | 1s
|  | 415 |  |  | Load Type | 43325 | 169/229 | 4CFD | 19709 | UInt | UInt | 0=Basic, 1=Load Curve, 2=Load Curv R
|  | 416 |  |  | Max Alarm
|  |  | 4161 |  | MaxAlarmMar | 43326 | 169/230 | 4CFE | 19710 | Long, 1=1% | EInt | 1%
|  |  | 4162 |  | MaxAlarmDel | 43330 | 169/234 | 4D02 | 19714 | Long, 1=0.1s | EInt | 0.1s
|  | 417 |  |  | Max PreAlarm
|  |  | 4171 |  | MaxPreAlMar | 43327 | 169/231 | 4CFF | 19711 | Long, 1=1% | EInt | 1%
|  |  | 4172 |  | MaxPreAlDel | 43331 | 169/235 | 4D03 | 19715 | Long, 1=0.1s | EInt | 0.1s
|  | 418 |  |  | Min PreAlarm
|  |  | 4181 |  | MinPreAlMar | 43328 | 169/232 | 4D00 | 19712 | Long, 1=1% | EInt | 1%
|  |  | 4182 |  | MinPreAlDel | 43332 | 169/236 | 4D04 | 19716 | Long, 1=0.1s | EInt | 0.1s
|  | 419 |  |  | Min Alarm
|  |  | 4191 |  | MinAlarmMar | 43329 | 169/233 | 4D01 | 19713 | Long, 1=1% | EInt | 1%
|  |  | 4192 |  | MinAlarmDel | 43333 | 169/237 | 4D05 | 19717 | Long, 1=0.1s | EInt | 0.1s
|  | 41A |  |  | Autoset Alrm | 43334 | 169/238 | 4D06 | 19718 | UInt | UInt | 0=No, 1=Yes
|  | 41B |  |  | Normal Load | 43335 | 169/239 | 4D07 | 19719 | Long, 1=1% | EInt | 1%
|  | 41C |  |  | Load Curve
|  |  | 41C1 |  | LoadCurve 1 | 43336 | 169/240 | 4D08 | 19720 | Long, 1=1% | EInt | 1%
[6 empty] | 43337 | 169/241 | 4D09 | 19721 | Int, 1=1rpm | Int | 1%
|  |  | 41C2 |  | LoadCurve 2 | 43338 | 169/242 | 4D0A | 19722 | Long, 1=1% | EInt | 1%
[6 empty] | 43339 | 169/243 | 4D0B | 19723 | Int, 1=1rpm | Int | 1%
|  |  | 41C3 |  | LoadCurve 3 | 43340 | 169/244 | 4D0C | 19724 | Long, 1=1% | EInt | 1%
[6 empty] | 43341 | 169/245 | 4D0D | 19725 | Int, 1=1rpm | Int | 1%
|  |  | 41C4 |  | LoadCurve 4 | 43342 | 169/246 | 4D0E | 19726 | Long, 1=1% | EInt | 1%
[6 empty] | 43343 | 169/247 | 4D0F | 19727 | Int, 1=1rpm | Int | 1%
|  |  | 41C5 |  | LoadCurve 5 | 43344 | 169/248 | 4D10 | 19728 | Long, 1=1% | EInt | 1%
[6 empty] | 43345 | 169/249 | 4D11 | 19729 | Int, 1=1rpm | Int | 1%
|  |  | 41C6 |  | LoadCurve 6 | 43346 | 169/250 | 4D12 | 19730 | Long, 1=1% | EInt | 1%
[6 empty] | 43347 | 169/251 | 4D13 | 19731 | Int, 1=1rpm | Int | 1%
|  |  | 41C7 |  | LoadCurve 7 | 43348 | 169/252 | 4D14 | 19732 | Long, 1=1% | EInt | 1%
[6 empty] | 43349 | 169/253 | 4D15 | 19733 | Int, 1=1rpm | Int | 1%
|  |  | 41C8 |  | LoadCurve 8 | 43350 | 169/254 | 4D16 | 19734 | Long, 1=1% | EInt | 1%
[6 empty] | 43351 | 170/0 | 4D17 | 19735 | Int, 1=1rpm | Int | 1%
|  |  | 41C9 |  | LoadCurve 9 | 43352 | 170/1 | 4D18 | 19736 | Long, 1=1% | EInt | 1%
[6 empty] | 43353 | 170/2 | 4D19 | 19737 | Int, 1=1rpm | Int | 1%
|  | 41D |  |  | MinAbsMarg | 43354 | 170/3 | 4D1A | 19738 | Long, 1=1% | EInt | 1%
| 420 |  |  |  | Process Prot
|  | 421 |  |  | Low Volt OR | 43361 | 170/10 | 4D21 | 19745 | UInt | UInt | 0=Off, 1=On
|  | 422 |  |  | Rotor Locked | 43362 | 170/11 | 4D22 | 19746 | UInt | UInt | 0=Off, 1=On
|  | 423 |  |  | Motor Lost | 43363 | 170/12 | 4D23 | 19747 | UInt | UInt | 0=Off, 1=Trip, 2=Start
|  | 424 |  |  | OverVolt Ctl | 43364 | 170/13 | 4D24 | 19748 | UInt | UInt | 0=Off, 1=On
| 430 |  |  |  | Trip Text
|  | 431 |  |  | ExtTrip1Text | 42457 | 166/126 | 4999 | 18841 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42458 | 166/127 | 499A | 18842 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42459 | 166/128 | 499B | 18843 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42460 | 166/129 | 499C | 18844 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42461 | 166/130 | 499D | 18845 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42462 | 166/131 | 499E | 18846 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42463 | 166/132 | 499F | 18847 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42464 | 166/133 | 49A0 | 18848 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42465 | 166/134 | 49A1 | 18849 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42466 | 166/135 | 49A2 | 18850 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42467 | 166/136 | 49A3 | 18851 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42468 | 166/137 | 49A4 | 18852 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
|  | 432 |  |  | ExtTrip2Text | 42469 | 166/138 | 49A5 | 18853 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42470 | 166/139 | 49A6 | 18854 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42471 | 166/140 | 49A7 | 18855 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42472 | 166/141 | 49A8 | 18856 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42473 | 166/142 | 49A9 | 18857 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42474 | 166/143 | 49AA | 18858 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42475 | 166/144 | 49AB | 18859 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42476 | 166/145 | 49AC | 18860 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42477 | 166/146 | 49AD | 18861 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42478 | 166/147 | 49AE | 18862 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42479 | 166/148 | 49AF | 18863 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42480 | 166/149 | 49B0 | 18864 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
|  | 433 |  |  | ExtTrip3Text | 42481 | 166/150 | 49B1 | 18865 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42482 | 166/151 | 49B2 | 18866 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42483 | 166/152 | 49B3 | 18867 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42484 | 166/153 | 49B4 | 18868 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42485 | 166/154 | 49B5 | 18869 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42486 | 166/155 | 49B6 | 18870 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42487 | 166/156 | 49B7 | 18871 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42488 | 166/157 | 49B8 | 18872 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42489 | 166/158 | 49B9 | 18873 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42490 | 166/159 | 49BA | 18874 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42491 | 166/160 | 49BB | 18875 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42492 | 166/161 | 49BC | 18876 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
|  | 434 |  |  | ExtTrip4Text | 42493 | 166/162 | 49BD | 18877 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42494 | 166/163 | 49BE | 18878 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42495 | 166/164 | 49BF | 18879 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42496 | 166/165 | 49C0 | 18880 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42497 | 166/166 | 49C1 | 18881 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42498 | 166/167 | 49C2 | 18882 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42499 | 166/168 | 49C3 | 18883 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42500 | 166/169 | 49C4 | 18884 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42501 | 166/170 | 49C5 | 18885 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42502 | 166/171 | 49C6 | 18886 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42503 | 166/172 | 49C7 | 18887 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42504 | 166/173 | 49C8 | 18888 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
500 |  |  |  |  | I/Os
| 510 |  |  |  | An Inputs
|  | 511 |  |  | AnIn1 Fc | 43201 | 169/105 | 4C81 | 19585 | UInt | UInt | 0=Off, 1=Max Speed, 2=Max Torque, 3=Process Val, 4=Process Ref, 5=Min Speed, 6=Option
|  | 512 |  |  | AnIn1 Setup | 43202 | 169/106 | 4C82 | 19586 | UInt | UInt | 0=4-20mA, 1=0-20mA, 2=User mA, 3=UserBipol mA, 4=0-10V, 5=2-10V, 6=User V, 7=User Bipol V
|  | 513 |  |  | AnIn1 Advan
|  |  | 5131 |  | AnIn1 Min | 43203 | 169/107 | 4C83 | 19587 | Long, 1=0.01 | EInt | 0.01mA, 0.01V
|  |  | 5132 |  | AnIn1 Max | 43204 | 169/108 | 4C84 | 19588 | Long, 1=0.01 | EInt | 0.01mA, 0.01V
|  |  | 5133 |  | AnIn1 Bipol | 43205 | 169/109 | 4C85 | 19589 | Long, 1=0.01 | EInt | 0.01mA, 0.01V
|  |  | 5134 |  | AnIn1 FcMin | 43206 | 169/110 | 4C86 | 19590 | UInt | UInt | 0=Min, 1=Max, 2=User defined
|  |  | 5135 |  | AnIn1 VaMin | 43541 | 170/190 | 4DD5 | 19925 | Long, 1=0.001 | EInt | 1rpm, 1%, 1°C, 0.001 in [322]
|  |  | 5136 |  | AnIn1 FcMax | 43207 | 169/111 | 4C87 | 19591 | UInt | UInt | 0=Min, 1=Max, 2=User defined
|  |  | 5137 |  | AnIn1 VaMax | 43551 | 170/200 | 4DDF | 19935 | Long, 1=0.001 | EInt | 1rpm, 1%, 1°C, 0.001 in [322]
|  |  | 5138 |  | AnIn1 Oper | 43208 | 169/112 | 4C88 | 19592 | UInt | UInt | 0=Add +, 1=Sub -
|  |  | 5139 |  | AnIn1 Filt | 43209 | 169/113 | 4C89 | 19593 | Long, 1=0.001s | EInt | 0.001s
|  |  | 513A |  | AnIn1 Enabl | 43210 | 169/114 | 4C8A | 19594 | UInt | UInt | 0=On, 1=!DigIn, 2=DigIn
|  | 514 |  |  | AnIn2 Fc | 43211 | 169/115 | 4C8B | 19595 | UInt | UInt | 0=Off, 1=Max Speed, 2=Max Torque, 3=Process Val, 4=Process Ref, 5=Min Speed, 6=Option
|  | 515 |  |  | AnIn2 Setup | 43212 | 169/116 | 4C8C | 19596 | UInt | UInt | 0=4-20mA, 1=0-20mA, 2=User mA, 3=UserBipol mA, 4=0-10V, 5=2-10V, 6=User V, 7=User Bipol V
|  | 516 |  |  | AnIn2 Advan
|  |  | 5161 |  | AnIn2 Min | 43213 | 169/117 | 4C8D | 19597 | Long, 1=0.01 | EInt | 0.01mA, 0.01V
|  |  | 5162 |  | AnIn2 Max | 43214 | 169/118 | 4C8E | 19598 | Long, 1=0.01 | EInt | 0.01mA, 0.01V
|  |  | 5163 |  | AnIn2 Bipol | 43215 | 169/119 | 4C8F | 19599 | Long, 1=0.01 | EInt | 0.01mA, 0.01V
|  |  | 5164 |  | AnIn2 FcMin | 43216 | 169/120 | 4C90 | 19600 | UInt | UInt | 0=Min, 1=Max, 2=User defined
|  |  | 5165 |  | AnIn2 VaMin | 43542 | 170/191 | 4DD6 | 19926 | Long, 1=0.001 | EInt | 1rpm, 1%, 1°C, 0.001 in [322]
|  |  | 5166 |  | AnIn2 FcMax | 43217 | 169/121 | 4C91 | 19601 | UInt | UInt | 0=Min, 1=Max, 2=User defined
|  |  | 5167 |  | AnIn2 VaMax | 43552 | 170/201 | 4DE0 | 19936 | Long, 1=0.001 | EInt | 1rpm, 1%, 1°C, 0.001 in [322]
|  |  | 5168 |  | AnIn2 Oper | 43218 | 169/122 | 4C92 | 19602 | UInt | UInt | 0=Add +, 1=Sub -
|  |  | 5169 |  | AnIn2 Filt | 43219 | 169/123 | 4C93 | 19603 | Long, 1=0.001s | EInt | 0.001s
|  |  | 516A |  | AnIn2 Enabl | 43220 | 169/124 | 4C94 | 19604 | UInt | UInt | 0=On, 1=!DigIn, 2=DigIn
|  | 517 |  |  | AnIn3 Fc | 43221 | 169/125 | 4C95 | 19605 | UInt | UInt | 0=Off, 1=Max Speed, 2=Max Torque, 3=Process Val, 4=Process Ref, 5=Min Speed, 6=Option
|  | 518 |  |  | AnIn3 Setup | 43222 | 169/126 | 4C96 | 19606 | UInt | UInt | 0=4-20mA, 1=0-20mA, 2=User mA, 3=UserBipol mA, 4=0-10V, 5=2-10V, 6=User V, 7=User Bipol V
|  | 519 |  |  | AnIn3 Advan
|  |  | 5191 |  | AnIn3 Min | 43223 | 169/127 | 4C97 | 19607 | Long, 1=0.01 | EInt | 0.01mA, 0.01V
|  |  | 5192 |  | AnIn3 Max | 43224 | 169/128 | 4C98 | 19608 | Long, 1=0.01 | EInt | 0.01mA, 0.01V
|  |  | 5193 |  | AnIn3 Bipol | 43225 | 169/129 | 4C99 | 19609 | Long, 1=0.01 | EInt | 0.01mA, 0.01V
|  |  | 5194 |  | AnIn3 FcMin | 43226 | 169/130 | 4C9A | 19610 | UInt | UInt | 0=Min, 1=Max, 2=User defined
|  |  | 5195 |  | AnIn3 VaMin | 43543 | 170/192 | 4DD7 | 19927 | Long, 1=0.001 | EInt | 1rpm, 1%, 1°C, 0.001 in [322]
|  |  | 5196 |  | AnIn3 FcMax | 43227 | 169/131 | 4C9B | 19611 | UInt | UInt | 0=Min, 1=Max, 2=User defined
|  |  | 5197 |  | AnIn3 VaMax | 43553 | 170/202 | 4DE1 | 19937 | Long, 1=0.001 | EInt | 1rpm, 1%, 1°C, 0.001 in [322]
|  |  | 5198 |  | AnIn3 Oper | 43228 | 169/132 | 4C9C | 19612 | UInt | UInt | 0=Add +, 1=Sub -
|  |  | 5199 |  | AnIn3 Filt | 43229 | 169/133 | 4C9D | 19613 | Long, 1=0.001s | EInt | 0.001s
|  |  | 519A |  | AnIn3 Enabl | 43230 | 169/134 | 4C9E | 19614 | UInt | UInt | 0=On, 1=!DigIn, 2=DigIn
|  | 51A |  |  | AnIn4 Fc | 43231 | 169/135 | 4C9F | 19615 | UInt | UInt | 0=Off, 1=Max Speed, 2=Max Torque, 3=Process Val, 4=Process Ref, 5=Min Speed, 6=Option
|  | 51B |  |  | AnIn4 Setup | 43232 | 169/136 | 4CA0 | 19616 | UInt | UInt | 0=4-20mA, 1=0-20mA, 2=User mA, 3=UserBipol mA, 4=0-10V, 5=2-10V, 6=User V, 7=User Bipol V
|  | 51C |  |  | AnIn4 Advan
|  |  | 51C1 |  | AnIn4 Min | 43233 | 169/137 | 4CA1 | 19617 | Long, 1=0.01 | EInt | 0.01mA, 0.01V
|  |  | 51C2 |  | AnIn4 Max | 43234 | 169/138 | 4CA2 | 19618 | Long, 1=0.01 | EInt | 0.01mA, 0.01V
|  |  | 51C3 |  | AnIn4 Bipol | 43235 | 169/139 | 4CA3 | 19619 | Long, 1=0.01 | EInt | 0.01mA, 0.01V
|  |  | 51C4 |  | AnIn4 FcMin | 43236 | 169/140 | 4CA4 | 19620 | UInt | UInt | 0=Min, 1=Max, 2=User defined
|  |  | 51C5 |  | AnIn4 VaMin | 43544 | 170/193 | 4DD8 | 19928 | Long, 1=0.001 | EInt | 1rpm, 1%, 1°C, 0.001 in [322]
|  |  | 51C6 |  | AnIn4 FcMax | 43237 | 169/141 | 4CA5 | 19621 | UInt | UInt | 0=Min, 1=Max, 2=User defined
|  |  | 51C7 |  | AnIn4 VaMax | 43554 | 170/203 | 4DE2 | 19938 | Long, 1=0.001 | EInt | 1rpm, 1%, 1°C, 0.001 in [322]
|  |  | 51C8 |  | AnIn4 Oper | 43238 | 169/142 | 4CA6 | 19622 | UInt | UInt | 0=Add +, 1=Sub -
|  |  | 51C9 |  | AnIn4 Filt | 43239 | 169/143 | 4CA7 | 19623 | Long, 1=0.001s | EInt | 0.001s
|  |  | 51CA |  | AnIn4 Enabl | 43240 | 169/144 | 4CA8 | 19624 | UInt | UInt | 0=On, 1=!DigIn, 2=DigIn
|  | 51D |  |  | AnIn Fault
|  |  | 51D1 |  | AnIn FltMode | 42859 | 168/18 | 4B2B | 19243 | UInt | UInt | 0=Off, 1=Trip, 2=Warning, 3=Change PSet, 4=Const Ref, 5=Last Ref
|  |  | 51D2 |  | AnIn FltRef | 42860 | 168/19 | 4B2C | 19244 | UInt, 1=1% | UInt | 1%
|  |  | 51D3 |  | AnIn Reset | 14 | 0/13 | 200E | 14 | UInt | UInt | 0=No, 1=Yes
| 520 |  |  |  | Dig Inputs
|  | 521 |  |  | DigIn 1 | 43241 | 169/145 | 4CA9 | 19625 | UInt | UInt | 0=Off, 1=Lim Switch+, 2=Lim Switch-, 3=Ext. Trip1, 4=Stop, 5=Enable, 6=RunR, 7=RunL, 8=Ext. Trip2, 9=Reset, 10=Preset Ctrl1, 11=Preset Ctrl2, 12=Preset Ctrl3, 13=MotPot Up, 14=MotPot Down, 15=Pump 1 Feedb, 16=Pump 2 Feedb, 17=Pump 3 Feedb, 18=Pump 4 Feedb, 19=Pump 5 Feedb, 20=Pump 6 Feedb, 21=Ext. Trip3, 22=Ext. Trip4, 23=Set Ctrl 1, 24=Set Ctrl 2, 25=Mot PreMag, 26=Jog, 27=Ext Mot Temp, 28=Loc/Rem, 29=AnIn Select, 30=LC Level, 31=Brk Ackn, 32=Sleep, 33=Fire Mode, 34=Timer 1, 35=Timer 2, 36=Timer 3, 37=Timer 4, 38=Option, 39=PumpClTrig, 40=PumpClBlock
|  | 522 |  |  | DigIn 2 | 43242 | 169/146 | 4CAA | 19626 | UInt | UInt | 0=Off, 1=Lim Switch+, 2=Lim Switch-, 3=Ext. Trip1, 4=Stop, 5=Enable, 6=RunR, 7=RunL, 8=Ext. Trip2, 9=Reset, 10=Preset Ctrl1, 11=Preset Ctrl2, 12=Preset Ctrl3, 13=MotPot Up, 14=MotPot Down, 15=Pump 1 Feedb, 16=Pump 2 Feedb, 17=Pump 3 Feedb, 18=Pump 4 Feedb, 19=Pump 5 Feedb, 20=Pump 6 Feedb, 21=Ext. Trip3, 22=Ext. Trip4, 23=Set Ctrl 1, 24=Set Ctrl 2, 25=Mot PreMag, 26=Jog, 27=Ext Mot Temp, 28=Loc/Rem, 29=AnIn Select, 30=LC Level, 31=Brk Ackn, 32=Sleep, 33=Fire Mode, 34=Timer 1, 35=Timer 2, 36=Timer 3, 37=Timer 4, 38=Option, 39=PumpClTrig, 40=PumpClBlock
|  | 523 |  |  | DigIn 3 | 43243 | 169/147 | 4CAB | 19627 | UInt | UInt | 0=Off, 1=Lim Switch+, 2=Lim Switch-, 3=Ext. Trip1, 4=Stop, 5=Enable, 6=RunR, 7=RunL, 8=Ext. Trip2, 9=Reset, 10=Preset Ctrl1, 11=Preset Ctrl2, 12=Preset Ctrl3, 13=MotPot Up, 14=MotPot Down, 15=Pump 1 Feedb, 16=Pump 2 Feedb, 17=Pump 3 Feedb, 18=Pump 4 Feedb, 19=Pump 5 Feedb, 20=Pump 6 Feedb, 21=Ext. Trip3, 22=Ext. Trip4, 23=Set Ctrl 1, 24=Set Ctrl 2, 25=Mot PreMag, 26=Jog, 27=Ext Mot Temp, 28=Loc/Rem, 29=AnIn Select, 30=LC Level, 31=Brk Ackn, 32=Sleep, 33=Fire Mode, 34=Timer 1, 35=Timer 2, 36=Timer 3, 37=Timer 4, 38=Option, 39=PumpClTrig, 40=PumpClBlock
|  | 524 |  |  | DigIn 4 | 43244 | 169/148 | 4CAC | 19628 | UInt | UInt | 0=Off, 1=Lim Switch+, 2=Lim Switch-, 3=Ext. Trip1, 4=Stop, 5=Enable, 6=RunR, 7=RunL, 8=Ext. Trip2, 9=Reset, 10=Preset Ctrl1, 11=Preset Ctrl2, 12=Preset Ctrl3, 13=MotPot Up, 14=MotPot Down, 15=Pump 1 Feedb, 16=Pump 2 Feedb, 17=Pump 3 Feedb, 18=Pump 4 Feedb, 19=Pump 5 Feedb, 20=Pump 6 Feedb, 21=Ext. Trip3, 22=Ext. Trip4, 23=Set Ctrl 1, 24=Set Ctrl 2, 25=Mot PreMag, 26=Jog, 27=Ext Mot Temp, 28=Loc/Rem, 29=AnIn Select, 30=LC Level, 31=Brk Ackn, 32=Sleep, 33=Fire Mode, 34=Timer 1, 35=Timer 2, 36=Timer 3, 37=Timer 4, 38=Option, 39=PumpClTrig, 40=PumpClBlock
|  | 525 |  |  | DigIn 5 | 43245 | 169/149 | 4CAD | 19629 | UInt | UInt | 0=Off, 1=Lim Switch+, 2=Lim Switch-, 3=Ext. Trip1, 4=Stop, 5=Enable, 6=RunR, 7=RunL, 8=Ext. Trip2, 9=Reset, 10=Preset Ctrl1, 11=Preset Ctrl2, 12=Preset Ctrl3, 13=MotPot Up, 14=MotPot Down, 15=Pump 1 Feedb, 16=Pump 2 Feedb, 17=Pump 3 Feedb, 18=Pump 4 Feedb, 19=Pump 5 Feedb, 20=Pump 6 Feedb, 21=Ext. Trip3, 22=Ext. Trip4, 23=Set Ctrl 1, 24=Set Ctrl 2, 25=Mot PreMag, 26=Jog, 27=Ext Mot Temp, 28=Loc/Rem, 29=AnIn Select, 30=LC Level, 31=Brk Ackn, 32=Sleep, 33=Fire Mode, 34=Timer 1, 35=Timer 2, 36=Timer 3, 37=Timer 4, 38=Option, 39=PumpClTrig, 40=PumpClBlock
|  | 526 |  |  | DigIn 6 | 43246 | 169/150 | 4CAE | 19630 | UInt | UInt | 0=Off, 1=Lim Switch+, 2=Lim Switch-, 3=Ext. Trip1, 4=Stop, 5=Enable, 6=RunR, 7=RunL, 8=Ext. Trip2, 9=Reset, 10=Preset Ctrl1, 11=Preset Ctrl2, 12=Preset Ctrl3, 13=MotPot Up, 14=MotPot Down, 15=Pump 1 Feedb, 16=Pump 2 Feedb, 17=Pump 3 Feedb, 18=Pump 4 Feedb, 19=Pump 5 Feedb, 20=Pump 6 Feedb, 21=Ext. Trip3, 22=Ext. Trip4, 23=Set Ctrl 1, 24=Set Ctrl 2, 25=Mot PreMag, 26=Jog, 27=Ext Mot Temp, 28=Loc/Rem, 29=AnIn Select, 30=LC Level, 31=Brk Ackn, 32=Sleep, 33=Fire Mode, 34=Timer 1, 35=Timer 2, 36=Timer 3, 37=Timer 4, 38=Option, 39=PumpClTrig, 40=PumpClBlock
|  | 527 |  |  | DigIn 7 | 43247 | 169/151 | 4CAF | 19631 | UInt | UInt | 0=Off, 1=Lim Switch+, 2=Lim Switch-, 3=Ext. Trip1, 4=Stop, 5=Enable, 6=RunR, 7=RunL, 8=Ext. Trip2, 9=Reset, 10=Preset Ctrl1, 11=Preset Ctrl2, 12=Preset Ctrl3, 13=MotPot Up, 14=MotPot Down, 15=Pump 1 Feedb, 16=Pump 2 Feedb, 17=Pump 3 Feedb, 18=Pump 4 Feedb, 19=Pump 5 Feedb, 20=Pump 6 Feedb, 21=Ext. Trip3, 22=Ext. Trip4, 23=Set Ctrl 1, 24=Set Ctrl 2, 25=Mot PreMag, 26=Jog, 27=Ext Mot Temp, 28=Loc/Rem, 29=AnIn Select, 30=LC Level, 31=Brk Ackn, 32=Sleep, 33=Fire Mode, 34=Timer 1, 35=Timer 2, 36=Timer 3, 37=Timer 4, 38=Option, 39=PumpClTrig, 40=PumpClBlock
|  | 528 |  |  | DigIn 8 | 43248 | 169/152 | 4CB0 | 19632 | UInt | UInt | 0=Off, 1=Lim Switch+, 2=Lim Switch-, 3=Ext. Trip1, 4=Stop, 5=Enable, 6=RunR, 7=RunL, 8=Ext. Trip2, 9=Reset, 10=Preset Ctrl1, 11=Preset Ctrl2, 12=Preset Ctrl3, 13=MotPot Up, 14=MotPot Down, 15=Pump 1 Feedb, 16=Pump 2 Feedb, 17=Pump 3 Feedb, 18=Pump 4 Feedb, 19=Pump 5 Feedb, 20=Pump 6 Feedb, 21=Ext. Trip3, 22=Ext. Trip4, 23=Set Ctrl 1, 24=Set Ctrl 2, 25=Mot PreMag, 26=Jog, 27=Ext Mot Temp, 28=Loc/Rem, 29=AnIn Select, 30=LC Level, 31=Brk Ackn, 32=Sleep, 33=Fire Mode, 34=Timer 1, 35=Timer 2, 36=Timer 3, 37=Timer 4, 38=Option, 39=PumpClTrig, 40=PumpClBlock
|  | 529 |  |  | B1 DigIn 1 | 43501 | 170/150 | 4DAD | 19885 | UInt | UInt | 0=Off, 1=Lim Switch+, 2=Lim Switch-, 3=Ext. Trip1, 4=Stop, 5=Enable, 6=RunR, 7=RunL, 8=Ext. Trip2, 9=Reset, 10=Preset Ctrl1, 11=Preset Ctrl2, 12=Preset Ctrl3, 13=MotPot Up, 14=MotPot Down, 15=Pump 1 Feedb, 16=Pump 2 Feedb, 17=Pump 3 Feedb, 18=Pump 4 Feedb, 19=Pump 5 Feedb, 20=Pump 6 Feedb, 21=Ext. Trip3, 22=Ext. Trip4, 23=Set Ctrl 1, 24=Set Ctrl 2, 25=Mot PreMag, 26=Jog, 27=Ext Mot Temp, 28=Loc/Rem, 29=AnIn Select, 30=LC Level, 31=Brk Ackn, 32=Sleep, 33=Fire Mode, 34=Timer 1, 35=Timer 2, 36=Timer 3, 37=Timer 4, 38=Option, 39=PumpClTrig, 40=PumpClBlock
|  | 52A |  |  | B1 DigIn 2 | 43502 | 170/151 | 4DAE | 19886 | UInt | UInt | 0=Off, 1=Lim Switch+, 2=Lim Switch-, 3=Ext. Trip1, 4=Stop, 5=Enable, 6=RunR, 7=RunL, 8=Ext. Trip2, 9=Reset, 10=Preset Ctrl1, 11=Preset Ctrl2, 12=Preset Ctrl3, 13=MotPot Up, 14=MotPot Down, 15=Pump 1 Feedb, 16=Pump 2 Feedb, 17=Pump 3 Feedb, 18=Pump 4 Feedb, 19=Pump 5 Feedb, 20=Pump 6 Feedb, 21=Ext. Trip3, 22=Ext. Trip4, 23=Set Ctrl 1, 24=Set Ctrl 2, 25=Mot PreMag, 26=Jog, 27=Ext Mot Temp, 28=Loc/Rem, 29=AnIn Select, 30=LC Level, 31=Brk Ackn, 32=Sleep, 33=Fire Mode, 34=Timer 1, 35=Timer 2, 36=Timer 3, 37=Timer 4, 38=Option, 39=PumpClTrig, 40=PumpClBlock
|  | 52B |  |  | B1 DigIn 3 | 43503 | 170/152 | 4DAF | 19887 | UInt | UInt | 0=Off, 1=Lim Switch+, 2=Lim Switch-, 3=Ext. Trip1, 4=Stop, 5=Enable, 6=RunR, 7=RunL, 8=Ext. Trip2, 9=Reset, 10=Preset Ctrl1, 11=Preset Ctrl2, 12=Preset Ctrl3, 13=MotPot Up, 14=MotPot Down, 15=Pump 1 Feedb, 16=Pump 2 Feedb, 17=Pump 3 Feedb, 18=Pump 4 Feedb, 19=Pump 5 Feedb, 20=Pump 6 Feedb, 21=Ext. Trip3, 22=Ext. Trip4, 23=Set Ctrl 1, 24=Set Ctrl 2, 25=Mot PreMag, 26=Jog, 27=Ext Mot Temp, 28=Loc/Rem, 29=AnIn Select, 30=LC Level, 31=Brk Ackn, 32=Sleep, 33=Fire Mode, 34=Timer 1, 35=Timer 2, 36=Timer 3, 37=Timer 4, 38=Option, 39=PumpClTrig, 40=PumpClBlock
|  | 52C |  |  | B2 DigIn 1 | 43504 | 170/153 | 4DB0 | 19888 | UInt | UInt | 0=Off, 1=Lim Switch+, 2=Lim Switch-, 3=Ext. Trip1, 4=Stop, 5=Enable, 6=RunR, 7=RunL, 8=Ext. Trip2, 9=Reset, 10=Preset Ctrl1, 11=Preset Ctrl2, 12=Preset Ctrl3, 13=MotPot Up, 14=MotPot Down, 15=Pump 1 Feedb, 16=Pump 2 Feedb, 17=Pump 3 Feedb, 18=Pump 4 Feedb, 19=Pump 5 Feedb, 20=Pump 6 Feedb, 21=Ext. Trip3, 22=Ext. Trip4, 23=Set Ctrl 1, 24=Set Ctrl 2, 25=Mot PreMag, 26=Jog, 27=Ext Mot Temp, 28=Loc/Rem, 29=AnIn Select, 30=LC Level, 31=Brk Ackn, 32=Sleep, 33=Fire Mode, 34=Timer 1, 35=Timer 2, 36=Timer 3, 37=Timer 4, 38=Option, 39=PumpClTrig, 40=PumpClBlock
|  | 52D |  |  | B2 DigIn 2 | 43505 | 170/154 | 4DB1 | 19889 | UInt | UInt | 0=Off, 1=Lim Switch+, 2=Lim Switch-, 3=Ext. Trip1, 4=Stop, 5=Enable, 6=RunR, 7=RunL, 8=Ext. Trip2, 9=Reset, 10=Preset Ctrl1, 11=Preset Ctrl2, 12=Preset Ctrl3, 13=MotPot Up, 14=MotPot Down, 15=Pump 1 Feedb, 16=Pump 2 Feedb, 17=Pump 3 Feedb, 18=Pump 4 Feedb, 19=Pump 5 Feedb, 20=Pump 6 Feedb, 21=Ext. Trip3, 22=Ext. Trip4, 23=Set Ctrl 1, 24=Set Ctrl 2, 25=Mot PreMag, 26=Jog, 27=Ext Mot Temp, 28=Loc/Rem, 29=AnIn Select, 30=LC Level, 31=Brk Ackn, 32=Sleep, 33=Fire Mode, 34=Timer 1, 35=Timer 2, 36=Timer 3, 37=Timer 4, 38=Option, 39=PumpClTrig, 40=PumpClBlock
|  | 52E |  |  | B2 DigIn 3 | 43506 | 170/155 | 4DB2 | 19890 | UInt | UInt | 0=Off, 1=Lim Switch+, 2=Lim Switch-, 3=Ext. Trip1, 4=Stop, 5=Enable, 6=RunR, 7=RunL, 8=Ext. Trip2, 9=Reset, 10=Preset Ctrl1, 11=Preset Ctrl2, 12=Preset Ctrl3, 13=MotPot Up, 14=MotPot Down, 15=Pump 1 Feedb, 16=Pump 2 Feedb, 17=Pump 3 Feedb, 18=Pump 4 Feedb, 19=Pump 5 Feedb, 20=Pump 6 Feedb, 21=Ext. Trip3, 22=Ext. Trip4, 23=Set Ctrl 1, 24=Set Ctrl 2, 25=Mot PreMag, 26=Jog, 27=Ext Mot Temp, 28=Loc/Rem, 29=AnIn Select, 30=LC Level, 31=Brk Ackn, 32=Sleep, 33=Fire Mode, 34=Timer 1, 35=Timer 2, 36=Timer 3, 37=Timer 4, 38=Option, 39=PumpClTrig, 40=PumpClBlock
|  | 52F |  |  | B3 DigIn 1 | 43507 | 170/156 | 4DB3 | 19891 | UInt | UInt | 0=Off, 1=Lim Switch+, 2=Lim Switch-, 3=Ext. Trip1, 4=Stop, 5=Enable, 6=RunR, 7=RunL, 8=Ext. Trip2, 9=Reset, 10=Preset Ctrl1, 11=Preset Ctrl2, 12=Preset Ctrl3, 13=MotPot Up, 14=MotPot Down, 15=Pump 1 Feedb, 16=Pump 2 Feedb, 17=Pump 3 Feedb, 18=Pump 4 Feedb, 19=Pump 5 Feedb, 20=Pump 6 Feedb, 21=Ext. Trip3, 22=Ext. Trip4, 23=Set Ctrl 1, 24=Set Ctrl 2, 25=Mot PreMag, 26=Jog, 27=Ext Mot Temp, 28=Loc/Rem, 29=AnIn Select, 30=LC Level, 31=Brk Ackn, 32=Sleep, 33=Fire Mode, 34=Timer 1, 35=Timer 2, 36=Timer 3, 37=Timer 4, 38=Option, 39=PumpClTrig, 40=PumpClBlock
|  | 52G |  |  | B3 DigIn 2 | 43508 | 170/157 | 4DB4 | 19892 | UInt | UInt | 0=Off, 1=Lim Switch+, 2=Lim Switch-, 3=Ext. Trip1, 4=Stop, 5=Enable, 6=RunR, 7=RunL, 8=Ext. Trip2, 9=Reset, 10=Preset Ctrl1, 11=Preset Ctrl2, 12=Preset Ctrl3, 13=MotPot Up, 14=MotPot Down, 15=Pump 1 Feedb, 16=Pump 2 Feedb, 17=Pump 3 Feedb, 18=Pump 4 Feedb, 19=Pump 5 Feedb, 20=Pump 6 Feedb, 21=Ext. Trip3, 22=Ext. Trip4, 23=Set Ctrl 1, 24=Set Ctrl 2, 25=Mot PreMag, 26=Jog, 27=Ext Mot Temp, 28=Loc/Rem, 29=AnIn Select, 30=LC Level, 31=Brk Ackn, 32=Sleep, 33=Fire Mode, 34=Timer 1, 35=Timer 2, 36=Timer 3, 37=Timer 4, 38=Option, 39=PumpClTrig, 40=PumpClBlock
|  | 52H |  |  | B3 DigIn 3 | 43509 | 170/158 | 4DB5 | 19893 | UInt | UInt | 0=Off, 1=Lim Switch+, 2=Lim Switch-, 3=Ext. Trip1, 4=Stop, 5=Enable, 6=RunR, 7=RunL, 8=Ext. Trip2, 9=Reset, 10=Preset Ctrl1, 11=Preset Ctrl2, 12=Preset Ctrl3, 13=MotPot Up, 14=MotPot Down, 15=Pump 1 Feedb, 16=Pump 2 Feedb, 17=Pump 3 Feedb, 18=Pump 4 Feedb, 19=Pump 5 Feedb, 20=Pump 6 Feedb, 21=Ext. Trip3, 22=Ext. Trip4, 23=Set Ctrl 1, 24=Set Ctrl 2, 25=Mot PreMag, 26=Jog, 27=Ext Mot Temp, 28=Loc/Rem, 29=AnIn Select, 30=LC Level, 31=Brk Ackn, 32=Sleep, 33=Fire Mode, 34=Timer 1, 35=Timer 2, 36=Timer 3, 37=Timer 4, 38=Option, 39=PumpClTrig, 40=PumpClBlock
| 530 |  |  |  | An Outputs
|  | 531 |  |  | AnOut1 Fc | 43251 | 169/155 | 4CB3 | 19635 | UInt | UInt | 0=Process Val, 1=Speed, 2=Torque, 3=Process Ref, 4=Shaft Power, 5=Frequency, 6=Current, 7=El Power, 8=Output volt, 9=DC Voltage, 10=AnIn1, 11=AnIn2, 12=AnIn3, 13=AnIn4, 14=Speed Ref, 15=Torque Ref, 16=AnMux1, 17=AnMux2, 18=IGBT Temp, 19=Option, 20=PT100_1, 21=PT100_2, 22=PT100_3
|  | 532 |  |  | AnOut1 Setup | 43252 | 169/156 | 4CB4 | 19636 | UInt | UInt | 0=4-20mA, 1=0-20mA, 2=User mA, 3=UserBipol mA, 4=0-10V, 5=2-10V, 6=User V, 7=User Bipol V
|  | 533 |  |  | AnOut1 Advan
|  |  | 5331 |  | AnOut1 Min | 43253 | 169/157 | 4CB5 | 19637 | Long, 1=0.01 | EInt | 0.01mA, 0.01V
|  |  | 5332 |  | AnOut1 Max | 43254 | 169/158 | 4CB6 | 19638 | Long, 1=0.01 | EInt | 0.01mA, 0.01V
|  |  | 5333 |  | AnOut1Bipol | 43255 | 169/159 | 4CB7 | 19639 | Long, 1=0.01 | EInt | 0.01mA, 0.01V
|  |  | 5334 |  | AnOut1FcMin | 43256 | 169/160 | 4CB8 | 19640 | UInt | UInt | 0=Min, 1=Max, 2=User defined
|  |  | 5335 |  | AnOut1VaMin | 43545 | 170/194 | 4DD9 | 19929 | Long, 1=0.001 | EInt | 1W, 0.1Hz, 0.1A, 0.1V, 1rpm, 1% or 0.001 in [322]
|  |  | 5336 |  | AnOut1FcMax | 43257 | 169/161 | 4CB9 | 19641 | UInt | UInt | 0=Min, 1=Max, 2=User defined
|  |  | 5337 |  | AnOut1VaMax | 43555 | 170/204 | 4DE3 | 19939 | Long, 1=0.001 | EInt | 1W, 0.1Hz, 0.1A, 0.1V, 1rpm, 1% or 0.001 in [322]
|  | 534 |  |  | AnOut2 Fc | 43261 | 169/165 | 4CBD | 19645 | UInt | UInt | 0=Process Val, 1=Speed, 2=Torque, 3=Process Ref, 4=Shaft Power, 5=Frequency, 6=Current, 7=El Power, 8=Output volt, 9=DC Voltage, 10=AnIn1, 11=AnIn2, 12=AnIn3, 13=AnIn4, 14=Speed Ref, 15=Torque Ref, 16=AnMux1, 17=AnMux2, 18=IGBT Temp, 19=Option, 20=PT100_1, 21=PT100_2, 22=PT100_3
|  | 535 |  |  | AnOut2 Setup | 43262 | 169/166 | 4CBE | 19646 | UInt | UInt | 0=4-20mA, 1=0-20mA, 2=User mA, 3=UserBipol mA, 4=0-10V, 5=2-10V, 6=User V, 7=User Bipol V
|  | 536 |  |  | AnOut2 Advan
|  |  | 5361 |  | AnOut2 Min | 43263 | 169/167 | 4CBF | 19647 | Long, 1=0.01 | EInt | 0.01mA, 0.01V
|  |  | 5362 |  | AnOut2 Max | 43264 | 169/168 | 4CC0 | 19648 | Long, 1=0.01 | EInt | 0.01mA, 0.01V
|  |  | 5363 |  | AnOut2Bipol | 43265 | 169/169 | 4CC1 | 19649 | Long, 1=0.01 | EInt | 0.01mA, 0.01V
|  |  | 5364 |  | AnOut2FcMin | 43266 | 169/170 | 4CC2 | 19650 | UInt | UInt | 0=Min, 1=Max, 2=User defined
|  |  | 5365 |  | AnOut2VaMin | 43546 | 170/195 | 4DDA | 19930 | Long, 1=0.001 | EInt | 1W, 0.1Hz, 0.1A, 0.1V, 1rpm, 1% or 0.001 in [322]
|  |  | 5366 |  | AnOut2FcMax | 43267 | 169/171 | 4CC3 | 19651 | UInt | UInt | 0=Min, 1=Max, 2=User defined
|  |  | 5367 |  | AnOut2VaMax | 43556 | 170/205 | 4DE4 | 19940 | Long, 1=0.001 | EInt | 1W, 0.1Hz, 0.1A, 0.1V, 1rpm, 1% or 0.001 in [322]
| 540 |  |  |  | Dig Outputs
|  | 541 |  |  | DigOut 1 | 43271 | 169/175 | 4CC7 | 19655 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  | 542 |  |  | DigOut 2 | 43272 | 169/176 | 4CC8 | 19656 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
| 550 |  |  |  | Relays
|  | 551 |  |  | Relay 1 | 43273 | 169/177 | 4CC9 | 19657 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  | 552 |  |  | Relay 2 | 43274 | 169/178 | 4CCA | 19658 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  | 553 |  |  | Relay 3 | 43275 | 169/179 | 4CCB | 19659 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  | 554 |  |  | B1 Relay 1 | 43511 | 170/160 | 4DB7 | 19895 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  | 555 |  |  | B1 Relay 2 | 43512 | 170/161 | 4DB8 | 19896 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  | 556 |  |  | B1 Relay 3 | 43513 | 170/162 | 4DB9 | 19897 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  | 557 |  |  | B2 Relay 1 | 43514 | 170/163 | 4DBA | 19898 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  | 558 |  |  | B2 Relay 2 | 43515 | 170/164 | 4DBB | 19899 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  | 559 |  |  | B2 Relay 3 | 43516 | 170/165 | 4DBC | 19900 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  | 55A |  |  | B3 Relay 1 | 43517 | 170/166 | 4DBD | 19901 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  | 55B |  |  | B3 Relay 2 | 43518 | 170/167 | 4DBE | 19902 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  | 55C |  |  | B3 Relay 3 | 43519 | 170/168 | 4DBF | 19903 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  | 55D |  |  | Relay Advan
|  |  | 55D1 |  | Relay1 Mode | 43276 | 169/180 | 4CCC | 19660 | UInt | UInt | 0=N.O, 1=N.C
|  |  | 55D2 |  | Relay2 Mode | 43277 | 169/181 | 4CCD | 19661 | UInt | UInt | 0=N.O, 1=N.C
|  |  | 55D3 |  | Relay3 Mode | 43278 | 169/182 | 4CCE | 19662 | UInt | UInt | 0=N.O, 1=N.C
|  |  | 55D4 |  | B1R1 Mode | 43521 | 170/170 | 4DC1 | 19905 | UInt | UInt | 0=N.O, 1=N.C
|  |  | 55D5 |  | B1R2 Mode | 43522 | 170/171 | 4DC2 | 19906 | UInt | UInt | 0=N.O, 1=N.C
|  |  | 55D6 |  | B1R3 Mode | 43523 | 170/172 | 4DC3 | 19907 | UInt | UInt | 0=N.O, 1=N.C
|  |  | 55D7 |  | B2R1 Mode | 43524 | 170/173 | 4DC4 | 19908 | UInt | UInt | 0=N.O, 1=N.C
|  |  | 55D8 |  | B2R2 Mode | 43525 | 170/174 | 4DC5 | 19909 | UInt | UInt | 0=N.O, 1=N.C
|  |  | 55D9 |  | B2R3 Mode | 43526 | 170/175 | 4DC6 | 19910 | UInt | UInt | 0=N.O, 1=N.C
|  |  | 55DA |  | B3R1 Mode | 43527 | 170/176 | 4DC7 | 19911 | UInt | UInt | 0=N.O, 1=N.C
|  |  | 55DB |  | B3R2 Mode | 43528 | 170/177 | 4DC8 | 19912 | UInt | UInt | 0=N.O, 1=N.C
|  |  | 55DC |  | B3R3 Mode | 43529 | 170/178 | 4DC9 | 19913 | UInt | UInt | 0=N.O, 1=N.C
| 560 |  |  |  | Virtual I/Os
|  | 561 |  |  | VIO 1 Dest | 43281 | 169/185 | 4CD1 | 19665 | UInt | UInt | 0=Off, 1=Lim Switch+, 2=Lim Switch-, 3=Ext. Trip1, 4=Stop, 5=Enable, 6=RunR, 7=RunL, 8=Ext. Trip2, 9=Reset, 10=Preset Ctrl1, 11=Preset Ctrl2, 12=Preset Ctrl3, 13=MotPot Up, 14=MotPot Down, 15=Pump 1 Feedb, 16=Pump 2 Feedb, 17=Pump 3 Feedb, 18=Pump 4 Feedb, 19=Pump 5 Feedb, 20=Pump 6 Feedb, 21=Ext. Trip3, 22=Ext. Trip4, 23=Set Ctrl 1, 24=Set Ctrl 2, 25=Mot PreMag, 26=Jog, 27=Ext Mot Temp, 28=Loc/Rem, 29=AnIn Select, 30=LC Level, 31=Brk Ackn, 32=Sleep, 33=Fire Mode, 34=Timer 1, 35=Timer 2, 36=Timer 3, 37=Timer 4, 38=Option, 39=PumpClTrig, 40=PumpClBlock
|  | 562 |  |  | VIO 1 Source | 43282 | 169/186 | 4CD2 | 19666 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  | 563 |  |  | VIO 2 Dest | 43283 | 169/187 | 4CD3 | 19667 | UInt | UInt | 0=Off, 1=Lim Switch+, 2=Lim Switch-, 3=Ext. Trip1, 4=Stop, 5=Enable, 6=RunR, 7=RunL, 8=Ext. Trip2, 9=Reset, 10=Preset Ctrl1, 11=Preset Ctrl2, 12=Preset Ctrl3, 13=MotPot Up, 14=MotPot Down, 15=Pump 1 Feedb, 16=Pump 2 Feedb, 17=Pump 3 Feedb, 18=Pump 4 Feedb, 19=Pump 5 Feedb, 20=Pump 6 Feedb, 21=Ext. Trip3, 22=Ext. Trip4, 23=Set Ctrl 1, 24=Set Ctrl 2, 25=Mot PreMag, 26=Jog, 27=Ext Mot Temp, 28=Loc/Rem, 29=AnIn Select, 30=LC Level, 31=Brk Ackn, 32=Sleep, 33=Fire Mode, 34=Timer 1, 35=Timer 2, 36=Timer 3, 37=Timer 4, 38=Option, 39=PumpClTrig, 40=PumpClBlock
|  | 564 |  |  | VIO 2 Source | 43284 | 169/188 | 4CD4 | 19668 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  | 565 |  |  | VIO 3 Dest | 43285 | 169/189 | 4CD5 | 19669 | UInt | UInt | 0=Off, 1=Lim Switch+, 2=Lim Switch-, 3=Ext. Trip1, 4=Stop, 5=Enable, 6=RunR, 7=RunL, 8=Ext. Trip2, 9=Reset, 10=Preset Ctrl1, 11=Preset Ctrl2, 12=Preset Ctrl3, 13=MotPot Up, 14=MotPot Down, 15=Pump 1 Feedb, 16=Pump 2 Feedb, 17=Pump 3 Feedb, 18=Pump 4 Feedb, 19=Pump 5 Feedb, 20=Pump 6 Feedb, 21=Ext. Trip3, 22=Ext. Trip4, 23=Set Ctrl 1, 24=Set Ctrl 2, 25=Mot PreMag, 26=Jog, 27=Ext Mot Temp, 28=Loc/Rem, 29=AnIn Select, 30=LC Level, 31=Brk Ackn, 32=Sleep, 33=Fire Mode, 34=Timer 1, 35=Timer 2, 36=Timer 3, 37=Timer 4, 38=Option, 39=PumpClTrig, 40=PumpClBlock
|  | 566 |  |  | VIO 3 Source | 43286 | 169/190 | 4CD6 | 19670 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  | 567 |  |  | VIO 4 Dest | 43287 | 169/191 | 4CD7 | 19671 | UInt | UInt | 0=Off, 1=Lim Switch+, 2=Lim Switch-, 3=Ext. Trip1, 4=Stop, 5=Enable, 6=RunR, 7=RunL, 8=Ext. Trip2, 9=Reset, 10=Preset Ctrl1, 11=Preset Ctrl2, 12=Preset Ctrl3, 13=MotPot Up, 14=MotPot Down, 15=Pump 1 Feedb, 16=Pump 2 Feedb, 17=Pump 3 Feedb, 18=Pump 4 Feedb, 19=Pump 5 Feedb, 20=Pump 6 Feedb, 21=Ext. Trip3, 22=Ext. Trip4, 23=Set Ctrl 1, 24=Set Ctrl 2, 25=Mot PreMag, 26=Jog, 27=Ext Mot Temp, 28=Loc/Rem, 29=AnIn Select, 30=LC Level, 31=Brk Ackn, 32=Sleep, 33=Fire Mode, 34=Timer 1, 35=Timer 2, 36=Timer 3, 37=Timer 4, 38=Option, 39=PumpClTrig, 40=PumpClBlock
|  | 568 |  |  | VIO 4 Source | 43288 | 169/192 | 4CD8 | 19672 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  | 569 |  |  | VIO 5 Dest | 43289 | 169/193 | 4CD9 | 19673 | UInt | UInt | 0=Off, 1=Lim Switch+, 2=Lim Switch-, 3=Ext. Trip1, 4=Stop, 5=Enable, 6=RunR, 7=RunL, 8=Ext. Trip2, 9=Reset, 10=Preset Ctrl1, 11=Preset Ctrl2, 12=Preset Ctrl3, 13=MotPot Up, 14=MotPot Down, 15=Pump 1 Feedb, 16=Pump 2 Feedb, 17=Pump 3 Feedb, 18=Pump 4 Feedb, 19=Pump 5 Feedb, 20=Pump 6 Feedb, 21=Ext. Trip3, 22=Ext. Trip4, 23=Set Ctrl 1, 24=Set Ctrl 2, 25=Mot PreMag, 26=Jog, 27=Ext Mot Temp, 28=Loc/Rem, 29=AnIn Select, 30=LC Level, 31=Brk Ackn, 32=Sleep, 33=Fire Mode, 34=Timer 1, 35=Timer 2, 36=Timer 3, 37=Timer 4, 38=Option, 39=PumpClTrig, 40=PumpClBlock
|  | 56A |  |  | VIO 5 Source | 43290 | 169/194 | 4CDA | 19674 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  | 56B |  |  | VIO 6 Dest | 43291 | 169/195 | 4CDB | 19675 | UInt | UInt | 0=Off, 1=Lim Switch+, 2=Lim Switch-, 3=Ext. Trip1, 4=Stop, 5=Enable, 6=RunR, 7=RunL, 8=Ext. Trip2, 9=Reset, 10=Preset Ctrl1, 11=Preset Ctrl2, 12=Preset Ctrl3, 13=MotPot Up, 14=MotPot Down, 15=Pump 1 Feedb, 16=Pump 2 Feedb, 17=Pump 3 Feedb, 18=Pump 4 Feedb, 19=Pump 5 Feedb, 20=Pump 6 Feedb, 21=Ext. Trip3, 22=Ext. Trip4, 23=Set Ctrl 1, 24=Set Ctrl 2, 25=Mot PreMag, 26=Jog, 27=Ext Mot Temp, 28=Loc/Rem, 29=AnIn Select, 30=LC Level, 31=Brk Ackn, 32=Sleep, 33=Fire Mode, 34=Timer 1, 35=Timer 2, 36=Timer 3, 37=Timer 4, 38=Option, 39=PumpClTrig, 40=PumpClBlock
|  | 56C |  |  | VIO 6 Source | 43292 | 169/196 | 4CDC | 19676 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  | 56D |  |  | VIO 7 Dest | 43293 | 169/197 | 4CDD | 19677 | UInt | UInt | 0=Off, 1=Lim Switch+, 2=Lim Switch-, 3=Ext. Trip1, 4=Stop, 5=Enable, 6=RunR, 7=RunL, 8=Ext. Trip2, 9=Reset, 10=Preset Ctrl1, 11=Preset Ctrl2, 12=Preset Ctrl3, 13=MotPot Up, 14=MotPot Down, 15=Pump 1 Feedb, 16=Pump 2 Feedb, 17=Pump 3 Feedb, 18=Pump 4 Feedb, 19=Pump 5 Feedb, 20=Pump 6 Feedb, 21=Ext. Trip3, 22=Ext. Trip4, 23=Set Ctrl 1, 24=Set Ctrl 2, 25=Mot PreMag, 26=Jog, 27=Ext Mot Temp, 28=Loc/Rem, 29=AnIn Select, 30=LC Level, 31=Brk Ackn, 32=Sleep, 33=Fire Mode, 34=Timer 1, 35=Timer 2, 36=Timer 3, 37=Timer 4, 38=Option, 39=PumpClTrig, 40=PumpClBlock
|  | 56E |  |  | VIO 7 Source | 43294 | 169/198 | 4CDE | 19678 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  | 56F |  |  | VIO 8 Dest | 43295 | 169/199 | 4CDF | 19679 | UInt | UInt | 0=Off, 1=Lim Switch+, 2=Lim Switch-, 3=Ext. Trip1, 4=Stop, 5=Enable, 6=RunR, 7=RunL, 8=Ext. Trip2, 9=Reset, 10=Preset Ctrl1, 11=Preset Ctrl2, 12=Preset Ctrl3, 13=MotPot Up, 14=MotPot Down, 15=Pump 1 Feedb, 16=Pump 2 Feedb, 17=Pump 3 Feedb, 18=Pump 4 Feedb, 19=Pump 5 Feedb, 20=Pump 6 Feedb, 21=Ext. Trip3, 22=Ext. Trip4, 23=Set Ctrl 1, 24=Set Ctrl 2, 25=Mot PreMag, 26=Jog, 27=Ext Mot Temp, 28=Loc/Rem, 29=AnIn Select, 30=LC Level, 31=Brk Ackn, 32=Sleep, 33=Fire Mode, 34=Timer 1, 35=Timer 2, 36=Timer 3, 37=Timer 4, 38=Option, 39=PumpClTrig, 40=PumpClBlock
|  | 56G |  |  | VIO 8 Source | 43296 | 169/200 | 4CE0 | 19680 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
600 |  |  |  |  | Logic&Timers
| 610 |  |  |  | Comparators
|  | 611 |  |  | CA1 Setup
|  |  | 6111 |  | CA1 Value | 43400 | 170/49 | 4D48 | 19784 | UInt | UInt | 0=Process Val, 1=Speed, 2=Torque, 3=Shaft Power, 4=El Power, 5=Current, 6=Output volt, 7=Frequency, 8=DC Voltage, 9=IGBT Temp, 10=PT100_1, 11=PT100_2, 12=PT100_3, 13=Energy, 14=Run Time, 15=Mains Time, 16=AnIn1, 17=AnIn2, 18=AnIn3, 19=AnIn4, 20=Process Ref, 21=Process Err, 22=PT100_4, 23=PT100_5, 24=PT100_6, 25=AnMux1, 26=AnMux2, 27=Speed Ref, 28=Torque Ref
|  |  | 6112 |  | CA1 LevelHI | 43401 | 170/50 | 4D49 | 19785 | Long, 1=0.001 | EInt | 1W, 0.1Hz, 0.1A, 0.1V, 1rpm, 1%, 0.1°C, 1kWh, 1h or 0.001 in [322]
|  |  | 6113 |  | CA1 LevelLO | 43402 | 170/51 | 4D4A | 19786 | Long, 1=0.001 | EInt | 1W, 0.1Hz, 0.1A, 0.1V, 1rpm, 1%, 0.1°C, 1kWh, 1h or 0.001 in [322]
|  |  | 6114 |  | CA1 Type | 43403 | 170/52 | 4D4B | 19787 | UInt | UInt | 0=Hysteresis, 1=Window
|  |  | 6115 |  | CA1 Polar | 43404 | 170/53 | 4D4C | 19788 | UInt | UInt | 0=Unipolar, 1=Bipolar
|  |  | 6116 |  | CA1 Set Dly | 43405 | 170/54 | 4D4D | 19789 | Long, 1=0.1s | EInt | 0.1s
|  |  | 6117 |  | CA1 Res Dly | 43406 | 170/55 | 4D4E | 19790 | Long, 1=0.1s | EInt | 0.1s
|  |  | 6118 |  | CA1 Tmr Val | 43407 | 170/56 | 4D4F | 19791 | Long, 1=0.1s | EInt | 0.1s
|  | 612 |  |  | CA2 Setup
|  |  | 6121 |  | CA2 Value | 43408 | 170/57 | 4D50 | 19792 | UInt | UInt | 0=Process Val, 1=Speed, 2=Torque, 3=Shaft Power, 4=El Power, 5=Current, 6=Output volt, 7=Frequency, 8=DC Voltage, 9=IGBT Temp, 10=PT100_1, 11=PT100_2, 12=PT100_3, 13=Energy, 14=Run Time, 15=Mains Time, 16=AnIn1, 17=AnIn2, 18=AnIn3, 19=AnIn4, 20=Process Ref, 21=Process Err, 22=PT100_4, 23=PT100_5, 24=PT100_6, 25=AnMux1, 26=AnMux2, 27=Speed Ref, 28=Torque Ref
|  |  | 6122 |  | CA2 LevelHI | 43409 | 170/58 | 4D51 | 19793 | Long, 1=0.001 | EInt | 1W, 0.1Hz, 0.1A, 0.1V, 1rpm, 1%, 0.1°C, 1kWh, 1h or 0.001 in [322]
|  |  | 6123 |  | CA2 LevelLO | 43410 | 170/59 | 4D52 | 19794 | Long, 1=0.001 | EInt | 1W, 0.1Hz, 0.1A, 0.1V, 1rpm, 1%, 0.1°C, 1kWh, 1h or 0.001 in [322]
|  |  | 6124 |  | CA2 Type | 43411 | 170/60 | 4D53 | 19795 | UInt | UInt | 0=Hysteresis, 1=Window
|  |  | 6125 |  | CA2 Polar | 43412 | 170/61 | 4D54 | 19796 | UInt | UInt | 0=Unipolar, 1=Bipolar
|  |  | 6126 |  | CA2 Set Dly | 43413 | 170/62 | 4D55 | 19797 | Long, 1=0.1s | EInt | 0.1s
|  |  | 6127 |  | CA2 Res Dly | 43414 | 170/63 | 4D56 | 19798 | Long, 1=0.1s | EInt | 0.1s
|  |  | 6128 |  | CA2 Tmr Val | 43415 | 170/64 | 4D57 | 19799 | Long, 1=0.1s | EInt | 0.1s
|  | 613 |  |  | CA3 Setup
|  |  | 6131 |  | CA3 Value | 43416 | 170/65 | 4D58 | 19800 | UInt | UInt | 0=Process Val, 1=Speed, 2=Torque, 3=Shaft Power, 4=El Power, 5=Current, 6=Output volt, 7=Frequency, 8=DC Voltage, 9=IGBT Temp, 10=PT100_1, 11=PT100_2, 12=PT100_3, 13=Energy, 14=Run Time, 15=Mains Time, 16=AnIn1, 17=AnIn2, 18=AnIn3, 19=AnIn4, 20=Process Ref, 21=Process Err, 22=PT100_4, 23=PT100_5, 24=PT100_6, 25=AnMux1, 26=AnMux2, 27=Speed Ref, 28=Torque Ref
|  |  | 6132 |  | CA3 LevelHI | 43417 | 170/66 | 4D59 | 19801 | Long, 1=0.001 | EInt | 1W, 0.1Hz, 0.1A, 0.1V, 1rpm, 1%, 0.1°C, 1kWh, 1h or 0.001 in [322]
|  |  | 6133 |  | CA3 LevelLO | 43418 | 170/67 | 4D5A | 19802 | Long, 1=0.001 | EInt | 1W, 0.1Hz, 0.1A, 0.1V, 1rpm, 1%, 0.1°C, 1kWh, 1h or 0.001 in [322]
|  |  | 6134 |  | CA3 Type | 43419 | 170/68 | 4D5B | 19803 | UInt | UInt | 0=Hysteresis, 1=Window
|  |  | 6135 |  | CA3 Polar | 43420 | 170/69 | 4D5C | 19804 | UInt | UInt | 0=Unipolar, 1=Bipolar
|  |  | 6136 |  | CA3 Set Dly | 43421 | 170/70 | 4D5D | 19805 | Long, 1=0.1s | EInt | 0.1s
|  |  | 6137 |  | CA3 Res Dly | 43422 | 170/71 | 4D5E | 19806 | Long, 1=0.1s | EInt | 0.1s
|  |  | 6138 |  | CA3 Tmr Val | 43423 | 170/72 | 4D5F | 19807 | Long, 1=0.1s | EInt | 0.1s
|  | 614 |  |  | CA4 Setup
|  |  | 6141 |  | CA4 Value | 43424 | 170/73 | 4D60 | 19808 | UInt | UInt | 0=Process Val, 1=Speed, 2=Torque, 3=Shaft Power, 4=El Power, 5=Current, 6=Output volt, 7=Frequency, 8=DC Voltage, 9=IGBT Temp, 10=PT100_1, 11=PT100_2, 12=PT100_3, 13=Energy, 14=Run Time, 15=Mains Time, 16=AnIn1, 17=AnIn2, 18=AnIn3, 19=AnIn4, 20=Process Ref, 21=Process Err, 22=PT100_4, 23=PT100_5, 24=PT100_6, 25=AnMux1, 26=AnMux2, 27=Speed Ref, 28=Torque Ref
|  |  | 6142 |  | CA4 LevelHI | 43425 | 170/74 | 4D61 | 19809 | Long, 1=0.001 | EInt | 1W, 0.1Hz, 0.1A, 0.1V, 1rpm, 1%, 0.1°C, 1kWh, 1h or 0.001 in [322]
|  |  | 6143 |  | CA4 LevelLO | 43426 | 170/75 | 4D62 | 19810 | Long, 1=0.001 | EInt | 1W, 0.1Hz, 0.1A, 0.1V, 1rpm, 1%, 0.1°C, 1kWh, 1h or 0.001 in [322]
|  |  | 6144 |  | CA4 Type | 43427 | 170/76 | 4D63 | 19811 | UInt | UInt | 0=Hysteresis, 1=Window
|  |  | 6145 |  | CA4 Polar | 43428 | 170/77 | 4D64 | 19812 | UInt | UInt | 0=Unipolar, 1=Bipolar
|  |  | 6146 |  | CA4 Set Dly | 43429 | 170/78 | 4D65 | 19813 | Long, 1=0.1s | EInt | 0.1s
|  |  | 6147 |  | CA4 Res Dly | 43430 | 170/79 | 4D66 | 19814 | Long, 1=0.1s | EInt | 0.1s
|  |  | 6148 |  | CA4 Tmr Val | 43431 | 170/80 | 4D67 | 19815 | Long, 1=0.1s | EInt | 0.1s
| 620 |  |  |  | Analog Mux
|  | 621 |  |  | AnMux1
|  |  | 6211 |  | AnMux1 InA | 43432 | 170/81 | 4D68 | 19816 | UInt | UInt | 0=AnIn1, 1=AnIn2, 2=AnIn3, 3=AnIn4
|  |  | 6212 |  | AnMux1 InB | 43433 | 170/82 | 4D69 | 19817 | UInt | UInt | 0=AnIn1, 1=AnIn2, 2=AnIn3, 3=AnIn4
|  |  | 6213 |  | AnMux1 Op | 43434 | 170/83 | 4D6A | 19818 | UInt | UInt | 0=Off, 1=MIN(A,B), 2=MAX(A,B), 3=A+B, 4=(A+B)/2, 5=A-B, 6=(A-B)/2, 7=B-A, 8=(B-A)/2, 9=ABS(A-B), 10=ABS(A-B)/2
|  | 622 |  |  | AnMux2
|  |  | 6221 |  | AnMux2 InA | 43435 | 170/84 | 4D6B | 19819 | UInt | UInt | 0=AnIn1, 1=AnIn2, 2=AnIn3, 3=AnIn4
|  |  | 6222 |  | AnMux2 InB | 43436 | 170/85 | 4D6C | 19820 | UInt | UInt | 0=AnIn1, 1=AnIn2, 2=AnIn3, 3=AnIn4
|  |  | 6223 |  | AnMux2 Op | 43437 | 170/86 | 4D6D | 19821 | UInt | UInt | 0=Off, 1=MIN(A,B), 2=MAX(A,B), 3=A+B, 4=(A+B)/2, 5=A-B, 6=(A-B)/2, 7=B-A, 8=(B-A)/2, 9=ABS(A-B), 10=ABS(A-B)/2
| 630 |  |  |  | Not Gate
|  | 631 |  |  | NOT1 Input | 43438 | 170/87 | 4D6E | 19822 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  | 632 |  |  | NOT2 Input | 43439 | 170/88 | 4D6F | 19823 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  | 633 |  |  | NOT3 Input | 43440 | 170/89 | 4D70 | 19824 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  | 634 |  |  | NOT4 Input | 43441 | 170/90 | 4D71 | 19825 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  | 635 |  |  | NOT5 Input | 43442 | 170/91 | 4D72 | 19826 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  | 636 |  |  | NOT6 Input | 43443 | 170/92 | 4D73 | 19827 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  | 637 |  |  | NOT7 Input | 43444 | 170/93 | 4D74 | 19828 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  | 638 |  |  | NOT8 Input | 43445 | 170/94 | 4D75 | 19829 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
| 640 |  |  |  | Logics
|  | 641 |  |  | Logic 1
|  |  | 6411 |  | L1 Expr | 43450 | 170/99 | 4D7A | 19834 | UInt | UInt | 0=((1.2).3).4, 1=(1.2).(3.4)
|  |  | 6412 |  | L1 Input 1 | 43451 | 170/100 | 4D7B | 19835 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  |  | 6413 |  | L1 Op 1 | 43452 | 170/101 | 4D7C | 19836 | UInt | UInt | 0=., 1=&, 2=+, 3=^
|  |  | 6414 |  | L1 Input 2 | 43453 | 170/102 | 4D7D | 19837 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  |  | 6415 |  | L1 Op 2 | 43454 | 170/103 | 4D7E | 19838 | UInt | UInt | 0=., 1=&, 2=+, 3=^
|  |  | 6416 |  | L1 Input 3 | 43455 | 170/104 | 4D7F | 19839 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  |  | 6417 |  | L1 Op 3 | 43456 | 170/105 | 4D80 | 19840 | UInt | UInt | 0=., 1=&, 2=+, 3=^
|  |  | 6418 |  | L1 Input 4 | 43457 | 170/106 | 4D81 | 19841 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  |  | 6419 |  | L1 Set Dly | 43458 | 170/107 | 4D82 | 19842 | Long, 1=0.1s | EInt | 0.1s
|  |  | 641A |  | L1 Res Dly | 43459 | 170/108 | 4D83 | 19843 | Long, 1=0.1s | EInt | 0.1s
|  |  | 641B |  | L1 Tmr Val | 43460 | 170/109 | 4D84 | 19844 | Long, 1=0.1s | EInt | 0.1s
|  | 642 |  |  | Logic 2
|  |  | 6421 |  | L2 Expr | 43461 | 170/110 | 4D85 | 19845 | UInt | UInt | 0=((1.2).3).4, 1=(1.2).(3.4)
|  |  | 6422 |  | L2 Input 1 | 43462 | 170/111 | 4D86 | 19846 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  |  | 6423 |  | L2 Op 1 | 43463 | 170/112 | 4D87 | 19847 | UInt | UInt | 0=., 1=&, 2=+, 3=^
|  |  | 6424 |  | L2 Input 2 | 43464 | 170/113 | 4D88 | 19848 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  |  | 6425 |  | L2 Op 2 | 43465 | 170/114 | 4D89 | 19849 | UInt | UInt | 0=., 1=&, 2=+, 3=^
|  |  | 6426 |  | L2 Input 3 | 43466 | 170/115 | 4D8A | 19850 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  |  | 6427 |  | L2 Op 3 | 43467 | 170/116 | 4D8B | 19851 | UInt | UInt | 0=., 1=&, 2=+, 3=^
|  |  | 6428 |  | L2 Input 4 | 43468 | 170/117 | 4D8C | 19852 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  |  | 6429 |  | L2 Set Dly | 43469 | 170/118 | 4D8D | 19853 | Long, 1=0.1s | EInt | 0.1s
|  |  | 642A |  | L2 Res Dly | 43470 | 170/119 | 4D8E | 19854 | Long, 1=0.1s | EInt | 0.1s
|  |  | 642B |  | L2 Tmr Val | 43471 | 170/120 | 4D8F | 19855 | Long, 1=0.1s | EInt | 0.1s
|  | 643 |  |  | Logic 3
|  |  | 6431 |  | L3 Expr | 43472 | 170/121 | 4D90 | 19856 | UInt | UInt | 0=((1.2).3).4, 1=(1.2).(3.4)
|  |  | 6432 |  | L3 Input 1 | 43473 | 170/122 | 4D91 | 19857 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  |  | 6433 |  | L3 Op 1 | 43474 | 170/123 | 4D92 | 19858 | UInt | UInt | 0=., 1=&, 2=+, 3=^
|  |  | 6434 |  | L3 Input 2 | 43475 | 170/124 | 4D93 | 19859 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  |  | 6435 |  | L3 Op 2 | 43476 | 170/125 | 4D94 | 19860 | UInt | UInt | 0=., 1=&, 2=+, 3=^
|  |  | 6436 |  | L3 Input 3 | 43477 | 170/126 | 4D95 | 19861 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  |  | 6437 |  | L3 Op 3 | 43478 | 170/127 | 4D96 | 19862 | UInt | UInt | 0=., 1=&, 2=+, 3=^
|  |  | 6438 |  | L3 Input 4 | 43479 | 170/128 | 4D97 | 19863 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  |  | 6439 |  | L3 Set Dly | 43480 | 170/129 | 4D98 | 19864 | Long, 1=0.1s | EInt | 0.1s
|  |  | 643A |  | L3 Res Dly | 43481 | 170/130 | 4D99 | 19865 | Long, 1=0.1s | EInt | 0.1s
|  |  | 643B |  | L3 Tmr Val | 43482 | 170/131 | 4D9A | 19866 | Long, 1=0.1s | EInt | 0.1s
|  | 644 |  |  | Logic 4
|  |  | 6441 |  | L4 Expr | 43483 | 170/132 | 4D9B | 19867 | UInt | UInt | 0=((1.2).3).4, 1=(1.2).(3.4)
|  |  | 6442 |  | L4 Input 1 | 43484 | 170/133 | 4D9C | 19868 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  |  | 6443 |  | L4 Op 1 | 43485 | 170/134 | 4D9D | 19869 | UInt | UInt | 0=., 1=&, 2=+, 3=^
|  |  | 6444 |  | L4 Input 2 | 43486 | 170/135 | 4D9E | 19870 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  |  | 6445 |  | L4 Op 2 | 43487 | 170/136 | 4D9F | 19871 | UInt | UInt | 0=., 1=&, 2=+, 3=^
|  |  | 6446 |  | L4 Input 3 | 43488 | 170/137 | 4DA0 | 19872 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  |  | 6447 |  | L4 Op 3 | 43489 | 170/138 | 4DA1 | 19873 | UInt | UInt | 0=., 1=&, 2=+, 3=^
|  |  | 6448 |  | L4 Input 4 | 43490 | 170/139 | 4DA2 | 19874 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  |  | 6449 |  | L4 Set Dly | 43491 | 170/140 | 4DA3 | 19875 | Long, 1=0.1s | EInt | 0.1s
|  |  | 644A |  | L4 Res Dly | 43492 | 170/141 | 4DA4 | 19876 | Long, 1=0.1s | EInt | 0.1s
|  |  | 644B |  | L4 Tmr Val | 43493 | 170/142 | 4DA5 | 19877 | Long, 1=0.1s | EInt | 0.1s
| 650 |  |  |  | Timers
|  | 651 |  |  | Timer1
|  |  | 6511 |  | Timer1 Trig | 43600 | 170/249 | 4E10 | 19984 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  |  | 6512 |  | Timer1 Mode | 43601 | 170/250 | 4E11 | 19985 | UInt | UInt | 0=Off, 1=Delay, 2=Alternate, 3=On-time
|  |  | 6514 |  | Timer1 T1/D | 43603 | 170/252 | 4E13 | 19987 | Long, 1=0.1s | EInt | 0.1s
|  |  | 6515 |  | Timer1 T2 | 43604 | 170/253 | 4E14 | 19988 | Long, 1=0.1s | EInt | 0.1s
|  |  | 6516 |  | Timer1Value | 43605 | 170/254 | 4E15 | 19989 | Long, 1=0.1s | EInt | 0.1s
|  | 652 |  |  | Timer2
|  |  | 6521 |  | Timer2 Trig | 43606 | 171/0 | 4E16 | 19990 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  |  | 6522 |  | Timer2 Mode | 43607 | 171/1 | 4E17 | 19991 | UInt | UInt | 0=Off, 1=Delay, 2=Alternate, 3=On-time
|  |  | 6524 |  | Timer2 T1/D | 43609 | 171/3 | 4E19 | 19993 | Long, 1=0.1s | EInt | 0.1s
|  |  | 6525 |  | Timer2 T2 | 43610 | 171/4 | 4E1A | 19994 | Long, 1=0.1s | EInt | 0.1s
|  |  | 6526 |  | Timer2Value | 43611 | 171/5 | 4E1B | 19995 | Long, 1=0.1s | EInt | 0.1s
|  | 653 |  |  | Timer3
|  |  | 6531 |  | Timer3 Trig | 43612 | 171/6 | 4E1C | 19996 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  |  | 6532 |  | Timer3 Mode | 43613 | 171/7 | 4E1D | 19997 | UInt | UInt | 0=Off, 1=Delay, 2=Alternate, 3=On-time
|  |  | 6534 |  | Timer3 T1/D | 43615 | 171/9 | 4E1F | 19999 | Long, 1=0.1s | EInt | 0.1s
|  |  | 6535 |  | Timer3 T2 | 43616 | 171/10 | 4E20 | 20000 | Long, 1=0.1s | EInt | 0.1s
|  |  | 6536 |  | Timer3Value | 43617 | 171/11 | 4E21 | 20001 | Long, 1=0.1s | EInt | 0.1s
|  | 654 |  |  | Timer4
|  |  | 6541 |  | Timer4 Trig | 43618 | 171/12 | 4E22 | 20002 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  |  | 6542 |  | Timer4 Mode | 43619 | 171/13 | 4E23 | 20003 | UInt | UInt | 0=Off, 1=Delay, 2=Alternate, 3=On-time
|  |  | 6544 |  | Timer4 T1/D | 43621 | 171/15 | 4E25 | 20005 | Long, 1=0.1s | EInt | 0.1s
|  |  | 6545 |  | Timer4 T2 | 43622 | 171/16 | 4E26 | 20006 | Long, 1=0.1s | EInt | 0.1s
|  |  | 6546 |  | Timer4Value | 43623 | 171/17 | 4E27 | 20007 | Long, 1=0.1s | EInt | 0.1s
| 660 |  |  |  | Flip flops
|  | 661 |  |  | Flip flop 1
|  |  | 6611 |  | F1 mode | 43630 | 171/24 | 4E2E | 20014 | UInt | UInt | 0=Reset, 1=Set, 2=Edge
|  |  | 6612 |  | F1 set | 43631 | 171/25 | 4E2F | 20015 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  |  | 6613 |  | F1 reset | 43632 | 171/26 | 4E30 | 20016 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  |  | 6614 |  | F1 Set Dly | 43633 | 171/27 | 4E31 | 20017 | Long, 1=0.1s | EInt | 0.1s
|  |  | 6615 |  | F1 Res Dly | 43634 | 171/28 | 4E32 | 20018 | Long, 1=0.1s | EInt | 0.1s
|  |  | 6616 |  | F1 Tmr Val | 43635 | 171/29 | 4E33 | 20019 | Long, 1=0.1s | EInt | 0.1s
|  | 662 |  |  | Flip flop 2
|  |  | 6621 |  | F2 mode | 43636 | 171/30 | 4E34 | 20020 | UInt | UInt | 0=Reset, 1=Set, 2=Edge
|  |  | 6622 |  | F2 set | 43637 | 171/31 | 4E35 | 20021 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  |  | 6623 |  | F2 reset | 43638 | 171/32 | 4E36 | 20022 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  |  | 6624 |  | F2 Set Dly | 43639 | 171/33 | 4E37 | 20023 | Long, 1=0.1s | EInt | 0.1s
|  |  | 6625 |  | F2 Res Dly | 43640 | 171/34 | 4E38 | 20024 | Long, 1=0.1s | EInt | 0.1s
|  |  | 6626 |  | F2 Tmr Val | 43641 | 171/35 | 4E39 | 20025 | Long, 1=0.1s | EInt | 0.1s
|  | 663 |  |  | Flip flop 3
|  |  | 6631 |  | F3 mode | 43642 | 171/36 | 4E3A | 20026 | UInt | UInt | 0=Reset, 1=Set, 2=Edge
|  |  | 6632 |  | F3 set | 43643 | 171/37 | 4E3B | 20027 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  |  | 6633 |  | F3 reset | 43644 | 171/38 | 4E3C | 20028 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  |  | 6634 |  | F3 Set Dly | 43645 | 171/39 | 4E3D | 20029 | Long, 1=0.1s | EInt | 0.1s
|  |  | 6635 |  | F3 Res Dly | 43646 | 171/40 | 4E3E | 20030 | Long, 1=0.1s | EInt | 0.1s
|  |  | 6636 |  | F3 Tmr Val | 43647 | 171/41 | 4E3F | 20031 | Long, 1=0.1s | EInt | 0.1s
|  | 664 |  |  | Flip flop 4
|  |  | 6641 |  | F4 mode | 43648 | 171/42 | 4E40 | 20032 | UInt | UInt | 0=Reset, 1=Set, 2=Edge
|  |  | 6642 |  | F4 set | 43649 | 171/43 | 4E41 | 20033 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  |  | 6643 |  | F4 reset | 43650 | 171/44 | 4E42 | 20034 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  |  | 6644 |  | F4 Set Dly | 43651 | 171/45 | 4E43 | 20035 | Long, 1=0.1s | EInt | 0.1s
|  |  | 6645 |  | F4 Res Dly | 43652 | 171/46 | 4E44 | 20036 | Long, 1=0.1s | EInt | 0.1s
|  |  | 6646 |  | F4 Tmr Val | 43653 | 171/47 | 4E45 | 20037 | Long, 1=0.1s | EInt | 0.1s
| 670 |  |  |  | Counters
|  | 671 |  |  | Counter1
|  |  | 6711 |  | C1 Trig | 43654 | 171/48 | 4E46 | 20038 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  |  | 6712 |  | C1 Reset | 43655 | 171/49 | 4E47 | 20039 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  |  | 6713 |  | C1 High Val | 43656 | 171/50 | 4E48 | 20040 | Long, 1=1 | EInt | 1
|  |  | 6714 |  | C1 Low Val | 43657 | 171/51 | 4E49 | 20041 | Long, 1=1 | EInt | 1
|  |  | 6715 |  | C1 DecTimer | 43658 | 171/52 | 4E4A | 20042 | Long, 1=1s | EInt | 1s
|  |  | 6719 |  | C1 Value | 43659 | 171/53 | 4E4B | 20043 | UInt, 1=1 | UInt | 1
|  | 672 |  |  | Counter2
|  |  | 6721 |  | C2 Trig | 43660 | 171/54 | 4E4C | 20044 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  |  | 6722 |  | C2 Reset | 43661 | 171/55 | 4E4D | 20045 | UInt | UInt | 0=Off, 1=On, 2=Run, 3=Stop, 4=0Hz, 5=Acc/Dec, 6=At process, 7=At Max spd, 8=No Trip, 9=Trip, 10=AutoRst Trip, 11=Limit, 12=Warning, 13=Ready, 14=T=Tlim, 15=I>Inom, 16=Brake, 17=AnIn<Offset, 18=Alarm, 19=Pre Alarm, 20=Max Alarm, 21=Max PreAlarm, 22=Min Alarm, 23=Min PreAlarm, 24=CA1, 25=CA2, 26=CA3, 27=CA4, 28=L1, 29=L2, 30=L3, 31=L4, 32=F1, 33=F2, 34=F3, 35=F4, 36=Operation, 37=T1Q, 38=T2Q, 39=T3Q, 40=T4Q, 41=Sleeping, 42=Crane Deviat, 43=PumpSlave1, 44=PumpSlave2, 45=PumpSlave3, 46=PumpSlave4, 47=PumpSlave5, 48=PumpSlave6, 49=PumpMaster1, 50=PumpMaster2, 51=PumpMaster3, 52=PumpMaster4, 53=PumpMaster5, 54=PumpMaster6, 55=All Pumps, 56=Only Master, 57=Loc/Rem, 58=Standby, 59=PTC Trip, 60=PT100 Trip, 61=Overvolt, 62=Overvolt G, 63=Overvolt D, 64=Acc, 65=Dec, 66=I²t, 67=V-Limit, 68=C-Limit, 69=Overtemp, 70=Low voltage, 71=DigIn 1, 72=DigIn 2, 73=DigIn 3, 74=DigIn 4, 75=DigIn 5, 76=DigIn 6, 77=DigIn 7, 78=DigIn 8, 79=ManRst Trip, 80=Com Error, 81=External Fan, 82=LC Pump, 83=LC HE Fan, 84=LC Level, 85=RunR, 86=RunL, 87=Com Active, 88=Brk Fault, 89=BrkNotEngage, 90=Option, 91=NOT1, 92=NOT2, 93=NOT3, 94=NOT4, 95=NOT5, 96=NOT6, 97=NOT7, 98=NOT8, 99=CTR1, 100=CTR2, 101=CLK1, 102=CLK2, 103=Enc Error, 104=Crane Comm, 105=Spin Start, 106=kWh-Pulses, 107=STO Active, 108=Spare, 109=ComFlt Set, 110=Fire Mode, 111=Option 1, 112=Option 2, 113=Option 3, 114=PumpClAct, 115=PumpClReq
|  |  | 6723 |  | C2 High Val | 43662 | 171/56 | 4E4E | 20046 | Long, 1=1 | EInt | 1
|  |  | 6724 |  | C2 Low Val | 43663 | 171/57 | 4E4F | 20047 | Long, 1=1 | EInt | 1
|  |  | 6725 |  | C2 DecTimer | 43664 | 171/58 | 4E50 | 20048 | Long, 1=1s | EInt | 1s
|  |  | 6729 |  | C2 Value | 43665 | 171/59 | 4E51 | 20049 | UInt, 1=1 | UInt | 1
| 680 |  |  |  | Clock logic
|  | 681 |  |  | Clock 1
|  |  | 6811 |  | Clk1TimeON | 43670 | 171/64 | 4E56 | 20054 | Long, 1=1h | EInt | 1h
[6 empty] | 43671 | 171/65 | 4E57 | 20055 | Long, 1=1m | EInt | 1m
[6 empty] | 43672 | 171/66 | 4E58 | 20056 | Long, 1=1s | EInt | 1s
|  |  | 6812 |  | Clk1TimeOff | 43673 | 171/67 | 4E59 | 20057 | Long, 1=1h | EInt | 1h
[6 empty] | 43674 | 171/68 | 4E5A | 20058 | Long, 1=1m | EInt | 1m
[6 empty] | 43675 | 171/69 | 4E5B | 20059 | Long, 1=1s | EInt | 1s
|  |  | 6813 |  | Clk1DateOn | 43676 | 171/70 | 4E5C | 20060 | Long, 1=1y | EInt | 1y
[6 empty] | 43677 | 171/71 | 4E5D | 20061 | Long, 1=1m | EInt | 1m
[6 empty] | 43678 | 171/72 | 4E5E | 20062 | Long, 1=1d | EInt | 1d
|  |  | 6814 |  | Clk1DateOff | 43679 | 171/73 | 4E5F | 20063 | Long, 1=1y | EInt | 1y
[6 empty] | 43680 | 171/74 | 4E60 | 20064 | Long, 1=1m | EInt | 1m
[6 empty] | 43681 | 171/75 | 4E61 | 20065 | Long, 1=1d | EInt | 1d
|  |  | 6815 |  | Clk1Weekday | 43682 | 171/76 | 4E62 | 20066 | UInt, 1=1 | UInt | 1
|  | 682 |  |  | Clock 2
|  |  | 6821 |  | Clk2TimeON | 43684 | 171/78 | 4E64 | 20068 | Long, 1=1h | EInt | 1h
[6 empty] | 43685 | 171/79 | 4E65 | 20069 | Long, 1=1m | EInt | 1m
[6 empty] | 43686 | 171/80 | 4E66 | 20070 | Long, 1=1s | EInt | 1s
|  |  | 6822 |  | Clk2TimeOff | 43687 | 171/81 | 4E67 | 20071 | Long, 1=1h | EInt | 1h
[6 empty] | 43688 | 171/82 | 4E68 | 20072 | Long, 1=1m | EInt | 1m
[6 empty] | 43689 | 171/83 | 4E69 | 20073 | Long, 1=1s | EInt | 1s
|  |  | 6823 |  | Clk2DateOn | 43690 | 171/84 | 4E6A | 20074 | Long, 1=1y | EInt | 1y
[6 empty] | 43691 | 171/85 | 4E6B | 20075 | Long, 1=1m | EInt | 1m
[6 empty] | 43692 | 171/86 | 4E6C | 20076 | Long, 1=1d | EInt | 1d
|  |  | 6824 |  | Clk2DateOff | 43693 | 171/87 | 4E6D | 20077 | Long, 1=1y | EInt | 1y
[6 empty] | 43694 | 171/88 | 4E6E | 20078 | Long, 1=1m | EInt | 1m
[6 empty] | 43695 | 171/89 | 4E6F | 20079 | Long, 1=1d | EInt | 1d
|  |  | 6825 |  | Clk2Weekday | 43696 | 171/90 | 4E70 | 20080 | UInt, 1=1 | UInt | 1
700 |  |  |  |  | Oper/Status
| 710 |  |  |  | Operation
|  | 711 |  |  | Process Val | 31001 | 121/145 | 23E9 | 1001 | Long, 1=0.001 | EInt | 1rpm, 1%, 1°C, 0.001 in [322]
|  | 712 |  |  | Speed | 31002 | 121/146 | 23EA | 1002 | Int, 1=1rpm | Int | 1rpm
|  | 713 |  |  | Torque | 31003 | 121/147 | 23EB | 1003 | Long, 1=0.1Nm | EInt | 0.1Nm
[6 empty] | 31004 | 121/148 | 23EC | 1004 | Long, 1=1% | EInt | 1%
|  | 714 |  |  | Shaft Power | 31005 | 121/149 | 23ED | 1005 | Long, 1=1W | EInt | 1W
|  | 715 |  |  | El Power | 31006 | 121/150 | 23EE | 1006 | Long, 1=1W | EInt | 1W
|  | 716 |  |  | Current | 31007 | 121/151 | 23EF | 1007 | Long, 1=0.1A | EInt | 0.1A
|  | 717 |  |  | Output volt | 31008 | 121/152 | 23F0 | 1008 | Long, 1=0.1V | EInt | 0.1V
|  | 718 |  |  | Frequency | 31009 | 121/153 | 23F1 | 1009 | Long, 1=0.1Hz | EInt | 0.1Hz
|  | 719 |  |  | DC Voltage | 31010 | 121/154 | 23F2 | 1010 | Long, 1=0.1V | EInt | 0.1V
|  | 71A |  |  | IGBT Temp | 31011 | 121/155 | 23F3 | 1011 | Long, 1=0.1°C | EInt | 0.1°C
|  | 71B |  |  | PT100 1,2,3 | 31012 | 121/156 | 23F4 | 1012 | Long, 1=1°C | EInt | 1°C
[6 empty] | 31013 | 121/157 | 23F5 | 1013 | Long, 1=1°C | EInt | 1°C
[6 empty] | 31014 | 121/158 | 23F6 | 1014 | Long, 1=1°C | EInt | 1°C
|  | 71C |  |  | PT100 4,5,6 | 31097 | 121/241 | 2449 | 1097 | Long, 1=1°C | EInt | 1°C
[6 empty] | 31098 | 121/242 | 244A | 1098 | Long, 1=1°C | EInt | 1°C
[6 empty] | 31099 | 121/243 | 244B | 1099 | Long, 1=1°C | EInt | 1°C
| 720 |  |  |  | Status
|  | 721 |  |  | VSD Status | 31015 | 121/159 | 23F7 | 1015 | UInt | UInt | Bit15=(0=NoTrip,1=Trip) / Bit14=(0=NoWarning,1=Warning) / Bit 13-8=Limit(0=No,1=VL,2=Sl,3=CL,4=TL) / Bit 7-5=RunCtrl(0=Rem,1=Key,2=Com,3=Opt) / Bit 4-2=RefCtrl(0=Rem,1=Key,2=Com,3=Opt) / Bit 1-0(LSB)=ParSet(0=A,1=B,2=C,3=D)
|  | 722 |  |  | Warning | 31016 | 121/160 | 23F8 | 1016 | UInt | UInt | 0=No Error, 1=Motor I²t, 2=PTC, 3=Motor Lost, 4=Locked rotor, 5=ExtTrip1, 6=Mon MaxAlarm, 7=Mon MinAlarm, 8=Comm error, 9=PT100, 10=Crane Deviat, 11=Pump, 12=Ext Mot Temp, 13=LC Level, 14=Brake, 15=Option, 16=Over temp, 17=Over curr F, 18=Over volt D, 19=Over volt G, 20=Over volt, 21=Over speed, 22=Under voltag, 23=Power fault, 24=Desat, 25=DClink error, 26=Int error, 27=Ovolt m cut, 28=Over voltage, 29=STO Active, 30=Crane Comm, 31=Encoder
|  | 723 |  |  | DigIn Status | 31017 | 121/161 | 23F9 | 1017 | UInt, 1=1 | UInt | Bit 7(MSB)=DigIn8 .. Bit 0(LSB)=DigIn1
|  | 724 |  |  | DigOutStatus | 31018 | 121/162 | 23FA | 1018 | UInt, 1=1 | UInt | Bit 10=Relay3 .. Bit 8=Relay1 / Bit 1=DigOut2 .. Bit 0(LSB)=DigOut1
|  | 725 |  |  | AnIn 1 2 | 31019 | 121/163 | 23FB | 1019 | Long, 1=1% | EInt | 1
[6 empty] | 31020 | 121/164 | 23FC | 1020 | Long, 1=1% | EInt | 1
|  | 726 |  |  | AnIn 3 4 | 31021 | 121/165 | 23FD | 1021 | Long, 1=1% | EInt | 1
[6 empty] | 31022 | 121/166 | 23FE | 1022 | Long, 1=1% | EInt | 1
|  | 727 |  |  | AnOut1 2 | 31023 | 121/167 | 23FF | 1023 | Long, 1=1% | EInt | 1
[6 empty] | 31024 | 121/168 | 2400 | 1024 | Long, 1=1% | EInt | 1
|  | 728 |  |  | IO Status B1 | 31025 | 121/169 | 2401 | 1025 | UInt, 1=1 | UInt | Bit 10=Relay3 .. Bit 8=Relay1 / Bit 2=DigIn3 .. Bit 0(LSB)=DigIn1
|  | 729 |  |  | IO Status B2 | 31026 | 121/170 | 2402 | 1026 | UInt, 1=1 | UInt | Bit 10=Relay3 .. Bit 8=Relay1 / Bit 2=DigIn3 .. Bit 0(LSB)=DigIn1
|  | 72A |  |  | IO Status B3 | 31027 | 121/171 | 2403 | 1027 | UInt, 1=1 | UInt | Bit 10=Relay3 .. Bit 8=Relay1 / Bit 2=DigIn3 .. Bit 0(LSB)=DigIn1
|  | 72B |  |  | Area D Stat
|  |  | 72B1 |  | Area D LSB | 30180 | 118/89 | 20B4 | 180 | UInt, 1=1 | UInt | Bit 15(MSB).. Bit 0(LSB)
|  |  | 72B2 |  | Area D MSB | 30182 | 118/91 | 20B6 | 182 | UInt, 1=1 | UInt | Bit 15(MSB).. Bit 0(LSB)
|  | 72C |  |  | VIO Status | 30181 | 118/90 | 20B5 | 181 | UInt, 1=1 | UInt | Bit 7(MSB)=DigIn8 .. Bit 0(LSB)=DigIn1
|  | 72D |  |  | Run Status | 31036 | 121/180 | 240C | 1036 | UInt | UInt | 0=OK, 1=No Run cmd, 2=No Enabl cmd, 3=Sleep, 4=Pump Blocked, 5=Trip, 6=STO, 7=Int Blocked, 8=PEBBs nok, 9=DC-link nok, 10=CP load/cpy, 11=Opt search, 12=Opt blocked
| 730 |  |  |  | Stored Val
|  | 731 |  |  | Run Time | 31028 | 121/172 | 2404 | 1028 | Long, 1=1h | EInt | 1h
[6 empty] | 31029 | 121/173 | 2405 | 1029 | Long, 1=1m | EInt | 1m
[6 empty] | 31030 | 121/174 | 2406 | 1030 | Long, 1=1s | EInt | 1s
|  |  | 7311 |  | Reset RunTm | 7 | 0/6 | 2007 | 7 | UInt | UInt | 0=No, 1=Yes
|  | 732 |  |  | Mains Time | 31031 | 121/175 | 2407 | 1031 | Long, 1=1h | EInt | 1h
[6 empty] | 31032 | 121/176 | 2408 | 1032 | Long, 1=1m | EInt | 1m
[6 empty] | 31033 | 121/177 | 2409 | 1033 | Long, 1=1s | EInt | 1s
|  | 733 |  |  | Energy | 31034 | 121/178 | 240A | 1034 | Long, 1=1Wh | EInt | 1Wh
|  |  | 7331 |  | Rst Energy | 6 | 0/5 | 2006 | 6 | UInt | UInt | 0=No, 1=Yes
800 |  |  |  |  | View TripLog
| 810 |  |  |  | Trip Message | 31101 | 121/245 | 244D | 1101 | UInt, 1=1 | UInt | 1
|  | 811 |  |  | Process Val | 31102 | 121/246 | 244E | 1102 | Long, 1=0.001 | EInt | 1rpm, 1%, 1°C, 0.001 in [322]
|  | 812 |  |  | Speed | 31103 | 121/247 | 244F | 1103 | Int, 1=1rpm | Int | 1rpm
|  | 813 |  |  | Torque | 31104 | 121/248 | 2450 | 1104 | Long, 1=0.1Nm | EInt | 0.1Nm
[6 empty] | 31105 | 121/249 | 2451 | 1105 | Long, 1=1% | EInt | 1%
|  | 814 |  |  | Shaft Power | 31106 | 121/250 | 2452 | 1106 | Long, 1=1W | EInt | 1W
|  | 815 |  |  | El Power | 31107 | 121/251 | 2453 | 1107 | Long, 1=1W | EInt | 1W
|  | 816 |  |  | Current | 31108 | 121/252 | 2454 | 1108 | Long, 1=0.1A | EInt | 0.1A
|  | 817 |  |  | Output volt | 31109 | 121/253 | 2455 | 1109 | Long, 1=0.1V | EInt | 0.1V
|  | 818 |  |  | Frequency | 31110 | 121/254 | 2456 | 1110 | Long, 1=0.1Hz | EInt | 0.1Hz
|  | 819 |  |  | DC Voltage | 31111 | 122/0 | 2457 | 1111 | Long, 1=0.1V | EInt | 0.1V
|  | 81A |  |  | IGBT Temp | 31112 | 122/1 | 2458 | 1112 | Long, 1=0.1°C | EInt | 0.1°C
|  | 81B |  |  | PT100 1,2,3 | 31113 | 122/2 | 2459 | 1113 | Long, 1=1°C | EInt | 1°C
[6 empty] | 31114 | 122/3 | 245A | 1114 | Long, 1=1°C | EInt | 1°C
[6 empty] | 31115 | 122/4 | 245B | 1115 | Long, 1=1°C | EInt | 1°C
|  | 81C |  |  | VSD Status | 31116 | 122/5 | 245C | 1116 | UInt | UInt | Bit15=(0=NoTrip,1=Trip) / Bit14=(0=NoWarning,1=Warning) / Bit 13-8=Limit(0=No,1=VL,2=Sl,3=CL,4=TL) / Bit 7-5=RunCtrl(0=Rem,1=Key,2=Com,3=Opt) / Bit 4-2=RefCtrl(0=Rem,1=Key,2=Com,3=Opt) / Bit 1-0(LSB)=ParSet(0=A,1=B,2=C,3=D)
|  | 81D |  |  | DigIn Status | 31117 | 122/6 | 245D | 1117 | UInt, 1=1 | UInt | Bit 7(MSB)=DigIn8 .. Bit 0(LSB)=DigIn1
|  | 81E |  |  | DigOutStatus | 31118 | 122/7 | 245E | 1118 | UInt, 1=1 | UInt | Bit 10=Relay3 .. Bit 8=Relay1 / Bit 1=DigOut2 .. Bit 0(LSB)=DigOut1
|  | 81F |  |  | AnIn 1 2 | 31119 | 122/8 | 245F | 1119 | Long, 1=1% | EInt | 1
[6 empty] | 31120 | 122/9 | 2460 | 1120 | Long, 1=1% | EInt | 1
|  | 81G |  |  | AnIn 3 4 | 31121 | 122/10 | 2461 | 1121 | Long, 1=1% | EInt | 1
[6 empty] | 31122 | 122/11 | 2462 | 1122 | Long, 1=1% | EInt | 1
|  | 81H |  |  | AnOut1 2 | 31123 | 122/12 | 2463 | 1123 | Long, 1=1% | EInt | 1
[6 empty] | 31124 | 122/13 | 2464 | 1124 | Long, 1=1% | EInt | 1
|  | 81I |  |  | IO Status B1 | 31125 | 122/14 | 2465 | 1125 | UInt, 1=1 | UInt | Bit 10=Relay3 .. Bit 8=Relay1 / Bit 2=DigIn3 .. Bit 0(LSB)=DigIn1
|  | 81J |  |  | IO Status B2 | 31126 | 122/15 | 2466 | 1126 | UInt, 1=1 | UInt | Bit 10=Relay3 .. Bit 8=Relay1 / Bit 2=DigIn3 .. Bit 0(LSB)=DigIn1
|  | 81K |  |  | IO Status B3 | 31127 | 122/16 | 2467 | 1127 | UInt, 1=1 | UInt | Bit 10=Relay3 .. Bit 8=Relay1 / Bit 2=DigIn3 .. Bit 0(LSB)=DigIn1
|  | 81L |  |  | Run Time | 31128 | 122/17 | 2468 | 1128 | Long, 1=1h | EInt | 1h
[6 empty] | 31129 | 122/18 | 2469 | 1129 | Long, 1=1m | EInt | 1m
[6 empty] | 31130 | 122/19 | 246A | 1130 | Long, 1=1s | EInt | 1s
|  | 81M |  |  | Mains Time | 31131 | 122/20 | 246B | 1131 | Long, 1=1h | EInt | 1h
[6 empty] | 31132 | 122/21 | 246C | 1132 | Long, 1=1m | EInt | 1m
[6 empty] | 31133 | 122/22 | 246D | 1133 | Long, 1=1s | EInt | 1s
|  | 81N |  |  | Energy | 31147 | 122/36 | 247B | 1147 | Long, 1=1Wh | EInt | 1Wh
|  | 81O |  |  | Set/View ref | 31135 | 122/24 | 246F | 1135 | Long, 1=0.001 | EInt | 1rpm, 1%, 1°C, 0.001 in [322]
|  | 81P |  |  | VIO Status | 31136 | 122/25 | 2470 | 1136 | UInt, 1=1 | UInt | Bit 7(MSB)=DigIn8 .. Bit 0(LSB)=DigIn1
|  | 81Q |  |  | PT100 4,5,6 | 31137 | 122/26 | 2471 | 1137 | Long, 1=1°C | EInt | 1°C
[6 empty] | 31138 | 122/27 | 2472 | 1138 | Long, 1=1°C | EInt | 1°C
[6 empty] | 31139 | 122/28 | 2473 | 1139 | Long, 1=1°C | EInt | 1°C
|  | 81R |  |  | Clock
|  |  | 81R1 |  | Time | 31141 | 122/30 | 2475 | 1141 | UInt, 1=1h | UInt | 1h
[6 empty] | 31142 | 122/31 | 2476 | 1142 | UInt, 1=1m | UInt | 1m
[6 empty] | 31143 | 122/32 | 2477 | 1143 | UInt, 1=1s | UInt | 1s
|  |  | 81R2 |  | Date | 31144 | 122/33 | 2478 | 1144 | UInt, 1=1y | UInt | 1y
[6 empty] | 31145 | 122/34 | 2479 | 1145 | UInt, 1=1m | UInt | 1m
[6 empty] | 31146 | 122/35 | 247A | 1146 | UInt, 1=1d | UInt | 1d
| 820 |  |  |  | Trip Message | 31151 | 122/40 | 247F | 1151
[5 empty] | (Log 2) | to | to | to | to
[6 empty] | 31196 | 122/85 | 24AC | 1196
| 830 |  |  |  | Trip Message | 31201 | 122/90 | 24B1 | 1201
[5 empty] | (Log 3) | to | to | to | to
[6 empty] | 31246 | 122/135 | 24DE | 1246
| 840 |  |  |  | Trip Message | 31251 | 122/140 | 24E3 | 1251
[5 empty] | (Log 4) | to | to | to | to
[6 empty] | 31296 | 122/185 | 2510 | 1296
| 850 |  |  |  | Trip Message | 31301 | 122/190 | 2515 | 1301
[5 empty] | (Log 5) | to | to | to | to
[6 empty] | 31346 | 122/235 | 2542 | 1346
| 860 |  |  |  | Trip Message | 31351 | 122/240 | 2547 | 1351
[5 empty] | (Log 6) | to | to | to | to
[6 empty] | 31396 | 123/30 | 2574 | 1396
| 870 |  |  |  | Trip Message | 31401 | 123/35 | 2579 | 1401
[5 empty] | (Log 7) | to | to | to | to
[6 empty] | 31446 | 123/80 | 25A6 | 1446
| 880 |  |  |  | Trip Message | 31451 | 123/85 | 25AB | 1451
[5 empty] | (Log 8) | to | to | to | to
[6 empty] | 31496 | 123/130 | 25D8 | 1496
| 890 |  |  |  | Trip Message | 31501 | 123/135 | 25DD | 1501
[5 empty] | (Log 9) | to | to | to | to
[6 empty] | 31546 | 123/180 | 260A | 1546
| 8A0 |  |  |  | Reset Trip L | 8 | 0/7 | 2008 | 8 | UInt | UInt | 0=No, 1=Yes
900 |  |  |  |  | System Data
| 920 |  |  |  | VSD Data
|  | 921 |  |  | VSD Type | 31037 | 121/181 | 240D | 1037 | UInt, 1=1 | UInt | 0=-
|  | 922 |  |  | Software | 31038 | 121/182 | 240E | 1038 | UInt | UInt | Bit 15(MSB)-14=Release type (0=V,1=P,2=b,3=a) .. Bit13-8=Major version .. Bit7-0(LSB)=Minor version
[6 empty] | 31039 | 121/183 | 240F | 1039 | UInt | UInt | Bit 15(MSB)-8=Major option version .. Bit7-0(LSB)=Minor option version
|  |  | 9221 |  | Build Info | 31040 | 121/184 | 2410 | 1040 | UInt | UInt | Year YY
[6 empty] | 31041 | 121/185 | 2411 | 1041 | UInt | UInt | Month MM
[6 empty] | 31042 | 121/186 | 2412 | 1042 | UInt | UInt | Date DD
[6 empty] | 31043 | 121/187 | 2413 | 1043 | UInt | UInt | Hour HH
[6 empty] | 31044 | 121/188 | 2414 | 1044 | UInt | UInt | Minute MM
[6 empty] | 31045 | 121/189 | 2415 | 1045 | UInt | UInt | Second SS
|  |  | 9222 |  | Build ID | 31048 | 121/192 | 2418 | 1048 | UInt, 1=1 | UInt | 1
|  |  | 9223 |  | EmoLib ID | 31049 | 121/193 | 2419 | 1049 | UInt, 1=1 | UInt | 1
|  |  | 9224 |  | SW Config | 31050 | 121/194 | 241A | 1050 | UInt, 1=1 | UInt | 1
|  | 923 |  |  | Unit Name | 42301 | 165/225 | 48FD | 18685 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42302 | 165/226 | 48FE | 18686 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42303 | 165/227 | 48FF | 18687 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42304 | 165/228 | 4900 | 18688 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42305 | 165/229 | 4901 | 18689 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42306 | 165/230 | 4902 | 18690 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42307 | 165/231 | 4903 | 18691 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42308 | 165/232 | 4904 | 18692 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42309 | 165/233 | 4905 | 18693 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42310 | 165/234 | 4906 | 18694 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42311 | 165/235 | 4907 | 18695 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42312 | 165/236 | 4908 | 18696 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
|  | 924 |  |  | Hardware
|  |  | 9241 |  | CB Key | 39900 | 156/119 | 46AC | 9900 | UInt, 1=1 | UInt | 1
|  | 925 |  |  | CtrlPanel
|  |  | 9251 |  | CP SW ver | 39901 | 156/120 | 46AD | 9901 | UInt | UInt | Bit 15(MSB)-14=Release type (0=V,1=P,2=b,3=a) .. Bit13-8=Major version .. Bit7-0(LSB)=Minor version
[6 empty] | 39902 | 156/121 | 46AE | 9902 | UInt | UInt | Bit 15(MSB)-8=Major option version .. Bit7-0(LSB)=Minor option version
|  |  | 9252 |  | CP HW ver | 39902 | 156/121 | 46AE | 9902 | UInt, 1=1 | UInt | 1
|  |  | 9253 |  | CP Build ID | 39903 | 156/122 | 46AF | 9903 | UInt, 1=1 | UInt | 1
|  |  | 9254 |  | CP Key | 39904 | 156/123 | 46B0 | 9904 | UInt, 1=1 | UInt | 1
| 930 |  |  |  | Clock
|  | 931 |  |  | Time | 42601 | 167/15 | 4A29 | 18985 | Long, 1=1h | EInt | 1h
[6 empty] | 42602 | 167/16 | 4A2A | 18986 | Long, 1=1m | EInt | 1m
[6 empty] | 42603 | 167/17 | 4A2B | 18987 | Long, 1=1s | EInt | 1s
|  | 932 |  |  | Date | 42604 | 167/18 | 4A2C | 18988 | Long, 1=1y | EInt | 1y
[6 empty] | 42605 | 167/19 | 4A2D | 18989 | Long, 1=1m | EInt | 1m
[6 empty] | 42606 | 167/20 | 4A2E | 18990 | Long, 1=1d | EInt | 1d
|  | 933 |  |  | Weekday | 42607 | 167/21 | 4A2F | 18991 | Long | EInt | 0=Monday, 1=Tuesday, 2=Wednesday, 3=Thursday, 4=Friday, 5=Saturday, 6=Sunday, 7=MTWTFSS
| 940 |  |  |  | Inspection
|  | 941 |  |  | Interval | 42651 | 167/65 | 4A5B | 19035 | Long, 1=1h | EInt | 1h
|  | 942 |  |  | Act.Counter | 42652 | 167/66 | 4A5C | 19036 | Long, 1=1h | EInt | 1h
|  | 943 |  |  | Clear Cnt | 10 | 0/9 | 200A | 10 | UInt | UInt | 0=No, 1=Yes
| 950 |  |  |  | Service Cont
|  | 951 |  |  | Company Name | 42351 | 166/20 | 492F | 18735 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42352 | 166/21 | 4930 | 18736 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42353 | 166/22 | 4931 | 18737 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42354 | 166/23 | 4932 | 18738 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42355 | 166/24 | 4933 | 18739 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42356 | 166/25 | 4934 | 18740 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42357 | 166/26 | 4935 | 18741 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42358 | 166/27 | 4936 | 18742 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42359 | 166/28 | 4937 | 18743 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42360 | 166/29 | 4938 | 18744 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42361 | 166/30 | 4939 | 18745 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42362 | 166/31 | 493A | 18746 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42363 | 166/32 | 493B | 18747 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42364 | 166/33 | 493C | 18748 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42365 | 166/34 | 493D | 18749 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42366 | 166/35 | 493E | 18750 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
|  | 952 |  |  | Phone Number | 42367 | 166/36 | 493F | 18751 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42368 | 166/37 | 4940 | 18752 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42369 | 166/38 | 4941 | 18753 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42370 | 166/39 | 4942 | 18754 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42371 | 166/40 | 4943 | 18755 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42372 | 166/41 | 4944 | 18756 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42373 | 166/42 | 4945 | 18757 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42374 | 166/43 | 4946 | 18758 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42375 | 166/44 | 4947 | 18759 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42376 | 166/45 | 4948 | 18760 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
|  | 953 |  |  | AddressLine1 | 42377 | 166/46 | 4949 | 18761 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42378 | 166/47 | 494A | 18762 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42379 | 166/48 | 494B | 18763 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42380 | 166/49 | 494C | 18764 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42381 | 166/50 | 494D | 18765 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42382 | 166/51 | 494E | 18766 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42383 | 166/52 | 494F | 18767 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42384 | 166/53 | 4950 | 18768 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42385 | 166/54 | 4951 | 18769 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42386 | 166/55 | 4952 | 18770 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42387 | 166/56 | 4953 | 18771 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42388 | 166/57 | 4954 | 18772 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42389 | 166/58 | 4955 | 18773 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42390 | 166/59 | 4956 | 18774 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42391 | 166/60 | 4957 | 18775 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42392 | 166/61 | 4958 | 18776 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
|  | 954 |  |  | AddressLine2 | 42393 | 166/62 | 4959 | 18777 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42394 | 166/63 | 495A | 18778 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42395 | 166/64 | 495B | 18779 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42396 | 166/65 | 495C | 18780 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42397 | 166/66 | 495D | 18781 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42398 | 166/67 | 495E | 18782 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42399 | 166/68 | 495F | 18783 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42400 | 166/69 | 4960 | 18784 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42401 | 166/70 | 4961 | 18785 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42402 | 166/71 | 4962 | 18786 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42403 | 166/72 | 4963 | 18787 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42404 | 166/73 | 4964 | 18788 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42405 | 166/74 | 4965 | 18789 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42406 | 166/75 | 4966 | 18790 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42407 | 166/76 | 4967 | 18791 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42408 | 166/77 | 4968 | 18792 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
|  | 955 |  |  | AddressLine3 | 42409 | 166/78 | 4969 | 18793 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42410 | 166/79 | 496A | 18794 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42411 | 166/80 | 496B | 18795 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42412 | 166/81 | 496C | 18796 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42413 | 166/82 | 496D | 18797 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42414 | 166/83 | 496E | 18798 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42415 | 166/84 | 496F | 18799 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42416 | 166/85 | 4970 | 18800 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42417 | 166/86 | 4971 | 18801 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42418 | 166/87 | 4972 | 18802 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42419 | 166/88 | 4973 | 18803 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42420 | 166/89 | 4974 | 18804 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42421 | 166/90 | 4975 | 18805 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42422 | 166/91 | 4976 | 18806 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42423 | 166/92 | 4977 | 18807 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42424 | 166/93 | 4978 | 18808 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
|  | 956 |  |  | Email Name | 42425 | 166/94 | 4979 | 18809 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42426 | 166/95 | 497A | 18810 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42427 | 166/96 | 497B | 18811 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42428 | 166/97 | 497C | 18812 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42429 | 166/98 | 497D | 18813 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42430 | 166/99 | 497E | 18814 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42431 | 166/100 | 497F | 18815 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42432 | 166/101 | 4980 | 18816 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42433 | 166/102 | 4981 | 18817 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42434 | 166/103 | 4982 | 18818 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42435 | 166/104 | 4983 | 18819 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42436 | 166/105 | 4984 | 18820 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42437 | 166/106 | 4985 | 18821 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42438 | 166/107 | 4986 | 18822 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42439 | 166/108 | 4987 | 18823 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42440 | 166/109 | 4988 | 18824 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
|  | 957 |  |  | Email Domain | 42441 | 166/110 | 4989 | 18825 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42442 | 166/111 | 498A | 18826 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42443 | 166/112 | 498B | 18827 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42444 | 166/113 | 498C | 18828 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42445 | 166/114 | 498D | 18829 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42446 | 166/115 | 498E | 18830 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42447 | 166/116 | 498F | 18831 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42448 | 166/117 | 4990 | 18832 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42449 | 166/118 | 4991 | 18833 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42450 | 166/119 | 4992 | 18834 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42451 | 166/120 | 4993 | 18835 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42452 | 166/121 | 4994 | 18836 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42453 | 166/122 | 4995 | 18837 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42454 | 166/123 | 4996 | 18838 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42455 | 166/124 | 4997 | 18839 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
[6 empty] | 42456 | 166/125 | 4998 | 18840 | UInt | UInt | See FDU-VFX2.1 Instruction Manual
Comm Params
[5 empty] | Reset | 42901 | 168/60 | 4B55 | 19285 | UInt | UInt
[5 empty] | Run | 42902 | 168/61 | 4B56 | 19286 | UInt | UInt
[5 empty] | RunR | 42903 | 168/62 | 4B57 | 19287 | UInt | UInt
[5 empty] | RunL | 42904 | 168/63 | 4B58 | 19288 | UInt | UInt
[5 empty] | Comm Ref | 42905 | 168/64 | 4B59 | 19289 | Int, 1=1 | Int | 1
[5 empty] | CommFeedback | 42906 | 168/65 | 4B5A | 19290 | Int, 1=1 | Int | 1
[5 empty] | Comm Set | 42907 | 168/66 | 4B5B | 19291 | UInt | UInt
[5 empty] | 32bit Reg 1 | 49770 | 195/44 | 662A | 26154 | UInt, 1=1 | UInt | 1
[5 empty] | 32bit Reg 2 | 49771 | 195/45 | 662B | 26155
[5 empty] | 32bit Reg 3 | 49772 | 195/46 | 662C | 26156
[5 empty] | 32bit Reg 4 | 49773 | 195/47 | 662D | 26157
[5 empty] | 32bit Reg 5 | 49774 | 195/48 | 662E | 26158
[5 empty] | 32bit Reg 6 | 49775 | 195/49 | 662F | 26159
[5 empty] | 32bit Reg 7 | 49776 | 195/50 | 6630 | 26160
[5 empty] | 32bit Reg 8 | 49777 | 195/51 | 6631 | 26161
[5 empty] | 32bit Reg 9 | 49778 | 195/52 | 6632 | 26162
[5 empty] | 32bit Reg 10 | 49779 | 195/53 | 6633 | 26163
[5 empty] | 32bit 1 LSB | 49780 | 195/54 | 6634 | 26164 | UInt, 1=1 | UInt | 1
[5 empty] | 32bit 1 MSB | 49781 | 195/55 | 6635 | 26165 | UInt, 1=1 | UInt | 1
[5 empty] | 32bit 2 LSB | 49782 | 195/56 | 6636 | 26166
[5 empty] | 32bit 2 MSB | 49783 | 195/57 | 6637 | 26167
[5 empty] | 32bit 3 LSB | 49784 | 195/58 | 6638 | 26168
[5 empty] | 32bit 3 MSB | 49785 | 195/59 | 6639 | 26169
[5 empty] | 32bit 4 LSB | 49786 | 195/60 | 663A | 26170
[5 empty] | 32bit 4 MSB | 49787 | 195/61 | 663B | 26171
[5 empty] | 32bit 5 LSB | 49788 | 195/62 | 663C | 26172
[5 empty] | 32bit 5 MSB | 49789 | 195/63 | 663D | 26173
[5 empty] | 32bit 6 LSB | 49790 | 195/64 | 663E | 26174
[5 empty] | 32bit 6 MSB | 49791 | 195/65 | 663F | 26175
[5 empty] | 32bit 7 LSB | 49792 | 195/66 | 6640 | 26176
[5 empty] | 32bit 7 MSB | 49793 | 195/67 | 6641 | 26177
[5 empty] | 32bit 8 LSB | 49794 | 195/68 | 6642 | 26178
[5 empty] | 32bit 8 MSB | 49795 | 195/69 | 6643 | 26179
[5 empty] | 32bit 9 LSB | 49796 | 195/70 | 6644 | 26180
[5 empty] | 32bit 9 MSB | 49797 | 195/71 | 6645 | 26181
[5 empty] | 32bit 10 LSB | 49798 | 195/72 | 6646 | 26182
[5 empty] | 32bit 10 MSB | 49799 | 195/73 | 6647 | 26183